## DC Cable Schedule
DC Cable Schedule
No | ID | String | Destination | Manufacturer | Model | Block ID | Size (mm2) | Outside Diameter (mm) | Bending Radius (nD) | Length (m) | Pos Length (m) | Neg Length (m) | Circuit Buried Length (m) | Vmp (V) | String Imp (A) | Resistance @ 90 (ohm/km) | Cable Vdrop (V) | Circuit Vdrop (V) | Circuit Vdrop (%) | Power Loss (W) | Power Loss (%)
1 | PCU01.INV1-BK-1_TS-0_TR0-TL0_S0 | 1-BK-1_TS-0_TR0-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2 | PCU01.INV1-BK-1_TS-0_TR0-TL0_S1 | 1-BK-1_TS-0_TR0-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
3 | PCU01.INV1-BK-1_TS-0_TR1-TL0_S0 | 1-BK-1_TS-0_TR1-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
4 | PCU01.INV1-BK-1_TS-0_TR1-TL0_S1 | 1-BK-1_TS-0_TR1-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
5 | PCU01.INV1-BK-1_TS-0_TR2-TL0_S0 | 1-BK-1_TS-0_TR2-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
6 | PCU01.INV1-BK-1_TS-0_TR2-TL0_S1 | 1-BK-1_TS-0_TR2-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
7 | PCU01.INV1-BK-1_TS-0_TR3-TL0_S0 | 1-BK-1_TS-0_TR3-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
8 | PCU01.INV1-BK-1_TS-0_TR3-TL0_S1 | 1-BK-1_TS-0_TR3-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
9 | PCU01.INV1-BK-1_TS-0_TR4-TL0_S0 | 1-BK-1_TS-0_TR4-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
10 | PCU01.INV1-BK-1_TS-0_TR4-TL0_S1 | 1-BK-1_TS-0_TR4-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
11 | PCU01.INV1-BK-1_TS-0_TR5-TL0_S0 | 1-BK-1_TS-0_TR5-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
12 | PCU01.INV1-BK-1_TS-0_TR5-TL0_S1 | 1-BK-1_TS-0_TR5-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
13 | PCU01.INV1-BK-1_TS-0_TR6-TL0_S0 | 1-BK-1_TS-0_TR6-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
14 | PCU01.INV1-BK-1_TS-0_TR6-TL0_S1 | 1-BK-1_TS-0_TR6-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
15 | PCU01.INV1-BK-1_TS-0_TR7-TL0_S0 | 1-BK-1_TS-0_TR7-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
16 | PCU01.INV1-BK-1_TS-0_TR7-TL0_S1 | 1-BK-1_TS-0_TR7-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
17 | PCU01.INV2-BK-1_TS-1_TR0-TL0_S0 | 1-BK-1_TS-1_TR0-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
18 | PCU01.INV2-BK-1_TS-1_TR0-TL0_S1 | 1-BK-1_TS-1_TR0-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
19 | PCU01.INV2-BK-1_TS-1_TR1-TL0_S0 | 1-BK-1_TS-1_TR1-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
20 | PCU01.INV2-BK-1_TS-1_TR1-TL0_S1 | 1-BK-1_TS-1_TR1-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
21 | PCU01.INV2-BK-1_TS-1_TR2-TL0_S0 | 1-BK-1_TS-1_TR2-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
22 | PCU01.INV2-BK-1_TS-1_TR2-TL0_S1 | 1-BK-1_TS-1_TR2-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
23 | PCU01.INV2-BK-1_TS-1_TR3-TL0_S0 | 1-BK-1_TS-1_TR3-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
24 | PCU01.INV2-BK-1_TS-1_TR3-TL0_S1 | 1-BK-1_TS-1_TR3-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
25 | PCU01.INV2-BK-1_TS-1_TR4-TL0_S0 | 1-BK-1_TS-1_TR4-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
26 | PCU01.INV2-BK-1_TS-1_TR4-TL0_S1 | 1-BK-1_TS-1_TR4-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
27 | PCU01.INV2-BK-1_TS-1_TR5-TL0_S0 | 1-BK-1_TS-1_TR5-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
28 | PCU01.INV2-BK-1_TS-1_TR5-TL0_S1 | 1-BK-1_TS-1_TR5-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
29 | PCU01.INV2-BK-1_TS-1_TR6-TL0_S0 | 1-BK-1_TS-1_TR6-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
30 | PCU01.INV2-BK-1_TS-1_TR6-TL0_S1 | 1-BK-1_TS-1_TR6-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
31 | PCU01.INV2-BK-1_TS-1_TR7-TL0_S0 | 1-BK-1_TS-1_TR7-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
32 | PCU01.INV2-BK-1_TS-1_TR7-TL0_S1 | 1-BK-1_TS-1_TR7-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
33 | PCU01.INV2-BK-1_TS-1_TR8-TL0_S0 | 1-BK-1_TS-1_TR8-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
34 | PCU01.INV2-BK-1_TS-1_TR8-TL0_S1 | 1-BK-1_TS-1_TR8-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
35 | PCU01.INV2-BK-1_TS-1_TR9-TL0_S1 | 1-BK-1_TS-1_TR9-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
36 | PCU01.INV3-BK-1_TS-1_TR9-TL0_S0 | 1-BK-1_TS-1_TR9-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
37 | PCU01.INV3-BK-1_TS-1_TR10-TL0_S0 | 1-BK-1_TS-1_TR10-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
38 | PCU01.INV3-BK-1_TS-1_TR10-TL0_S1 | 1-BK-1_TS-1_TR10-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
39 | PCU01.INV3-BK-1_TS-1_TR11-TL0_S0 | 1-BK-1_TS-1_TR11-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
40 | PCU01.INV3-BK-1_TS-1_TR11-TL0_S1 | 1-BK-1_TS-1_TR11-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
41 | PCU01.INV3-BK-1_TS-1_TR12-TL0_S0 | 1-BK-1_TS-1_TR12-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
42 | PCU01.INV3-BK-1_TS-1_TR12-TL0_S1 | 1-BK-1_TS-1_TR12-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
43 | PCU01.INV3-BK-1_TS-1_TR13-TL0_S0 | 1-BK-1_TS-1_TR13-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
44 | PCU01.INV3-BK-1_TS-1_TR13-TL0_S1 | 1-BK-1_TS-1_TR13-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
45 | PCU01.INV3-BK-1_TS-1_TR14-TL0_S0 | 1-BK-1_TS-1_TR14-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
46 | PCU01.INV3-BK-1_TS-1_TR14-TL0_S1 | 1-BK-1_TS-1_TR14-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
47 | PCU01.INV3-BK-1_TS-1_TR15-TL0_S0 | 1-BK-1_TS-1_TR15-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
48 | PCU01.INV3-BK-1_TS-1_TR15-TL0_S1 | 1-BK-1_TS-1_TR15-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
49 | PCU01.INV3-BK-1_TS-1_TR16-TL0_S0 | 1-BK-1_TS-1_TR16-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
50 | PCU01.INV3-BK-1_TS-1_TR16-TL0_S1 | 1-BK-1_TS-1_TR16-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
51 | PCU01.INV3-BK-1_TS-1_TR17-TL0_S0 | 1-BK-1_TS-1_TR17-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
52 | PCU01.INV3-BK-1_TS-1_TR17-TL0_S1 | 1-BK-1_TS-1_TR17-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
53 | PCU01.INV3-BK-1_TS-1_TR18-TL0_S0 | 1-BK-1_TS-1_TR18-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
54 | PCU01.INV3-BK-1_TS-1_TR18-TL0_S1 | 1-BK-1_TS-1_TR18-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
55 | PCU01.INV4-BK-1_TS-1_TR19-TL0_S0 | 1-BK-1_TS-1_TR19-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
56 | PCU01.INV4-BK-1_TS-1_TR19-TL0_S1 | 1-BK-1_TS-1_TR19-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
57 | PCU01.INV4-BK-1_TS-1_TR20-TL0_S0 | 1-BK-1_TS-1_TR20-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
58 | PCU01.INV4-BK-1_TS-1_TR20-TL0_S1 | 1-BK-1_TS-1_TR20-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
59 | PCU01.INV4-BK-1_TS-1_TR21-TL0_S0 | 1-BK-1_TS-1_TR21-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
60 | PCU01.INV4-BK-1_TS-1_TR21-TL0_S1 | 1-BK-1_TS-1_TR21-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
61 | PCU01.INV4-BK-1_TS-1_TR22-TL0_S0 | 1-BK-1_TS-1_TR22-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
62 | PCU01.INV4-BK-1_TS-1_TR22-TL0_S1 | 1-BK-1_TS-1_TR22-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
63 | PCU01.INV4-BK-1_TS-1_TR23-TL0_S0 | 1-BK-1_TS-1_TR23-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
64 | PCU01.INV4-BK-1_TS-1_TR23-TL0_S1 | 1-BK-1_TS-1_TR23-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
65 | PCU01.INV4-BK-1_TS-1_TR24-TL0_S0 | 1-BK-1_TS-1_TR24-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
66 | PCU01.INV4-BK-1_TS-1_TR24-TL0_S1 | 1-BK-1_TS-1_TR24-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
67 | PCU01.INV4-BK-1_TS-1_TR25-TL0_S0 | 1-BK-1_TS-1_TR25-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
68 | PCU01.INV4-BK-1_TS-1_TR25-TL0_S1 | 1-BK-1_TS-1_TR25-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
69 | PCU01.INV4-BK-1_TS-1_TR26-TL0_S0 | 1-BK-1_TS-1_TR26-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
70 | PCU01.INV4-BK-1_TS-1_TR26-TL0_S1 | 1-BK-1_TS-1_TR26-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
71 | PCU01.INV4-BK-1_TS-1_TR27-TL0_S0 | 1-BK-1_TS-1_TR27-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
72 | PCU01.INV4-BK-1_TS-1_TR27-TL0_S1 | 1-BK-1_TS-1_TR27-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
73 | PCU01.INV5-BK-1_TS-1_TR28-TL0_S0 | 1-BK-1_TS-1_TR28-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
74 | PCU01.INV5-BK-1_TS-1_TR28-TL0_S1 | 1-BK-1_TS-1_TR28-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
75 | PCU01.INV5-BK-1_TS-1_TR29-TL0_S0 | 1-BK-1_TS-1_TR29-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
76 | PCU01.INV5-BK-1_TS-1_TR29-TL0_S1 | 1-BK-1_TS-1_TR29-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
77 | PCU01.INV5-BK-1_TS-1_TR30-TL0_S0 | 1-BK-1_TS-1_TR30-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
78 | PCU01.INV5-BK-1_TS-1_TR30-TL0_S1 | 1-BK-1_TS-1_TR30-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
79 | PCU01.INV5-BK-1_TS-1_TR31-TL0_S0 | 1-BK-1_TS-1_TR31-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
80 | PCU01.INV5-BK-1_TS-1_TR31-TL0_S1 | 1-BK-1_TS-1_TR31-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
81 | PCU01.INV5-BK-1_TS-1_TR32-TL0_S0 | 1-BK-1_TS-1_TR32-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
82 | PCU01.INV5-BK-1_TS-1_TR32-TL0_S1 | 1-BK-1_TS-1_TR32-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
83 | PCU01.INV5-BK-1_TS-1_TR33-TL0_S0 | 1-BK-1_TS-1_TR33-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
84 | PCU01.INV5-BK-1_TS-1_TR33-TL0_S1 | 1-BK-1_TS-1_TR33-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
85 | PCU01.INV5-BK-1_TS-1_TR34-TL0_S0 | 1-BK-1_TS-1_TR34-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
86 | PCU01.INV5-BK-1_TS-1_TR34-TL0_S1 | 1-BK-1_TS-1_TR34-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
87 | PCU01.INV5-BK-1_TS-1_TR35-TL0_S0 | 1-BK-1_TS-1_TR35-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
88 | PCU01.INV5-BK-1_TS-1_TR35-TL0_S1 | 1-BK-1_TS-1_TR35-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
89 | PCU01.INV5-BK-1_TS-1_TR36-TL0_S0 | 1-BK-1_TS-1_TR36-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
90 | PCU01.INV5-BK-1_TS-1_TR36-TL0_S1 | 1-BK-1_TS-1_TR36-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
91 | PCU01.INV6-BK-1_TS-1_TR37-TL0_S0 | 1-BK-1_TS-1_TR37-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
92 | PCU01.INV6-BK-1_TS-1_TR37-TL0_S1 | 1-BK-1_TS-1_TR37-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
93 | PCU01.INV6-BK-1_TS-1_TR38-TL0_S0 | 1-BK-1_TS-1_TR38-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
94 | PCU01.INV6-BK-1_TS-1_TR38-TL0_S1 | 1-BK-1_TS-1_TR38-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
95 | PCU01.INV6-BK-1_TS-1_TR39-TL0_S0 | 1-BK-1_TS-1_TR39-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
96 | PCU01.INV6-BK-1_TS-1_TR39-TL0_S1 | 1-BK-1_TS-1_TR39-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
97 | PCU01.INV6-BK-1_TS-1_TR40-TL0_S0 | 1-BK-1_TS-1_TR40-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
98 | PCU01.INV6-BK-1_TS-1_TR40-TL0_S1 | 1-BK-1_TS-1_TR40-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
99 | PCU01.INV6-BK-1_TS-1_TR41-TL0_S0 | 1-BK-1_TS-1_TR41-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
100 | PCU01.INV6-BK-1_TS-1_TR41-TL0_S1 | 1-BK-1_TS-1_TR41-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
101 | PCU01.INV6-BK-1_TS-1_TR42-TL0_S0 | 1-BK-1_TS-1_TR42-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
102 | PCU01.INV6-BK-1_TS-1_TR42-TL0_S1 | 1-BK-1_TS-1_TR42-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
103 | PCU01.INV6-BK-1_TS-1_TR43-TL0_S0 | 1-BK-1_TS-1_TR43-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
104 | PCU01.INV6-BK-1_TS-1_TR43-TL0_S1 | 1-BK-1_TS-1_TR43-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
105 | PCU01.INV6-BK-1_TS-1_TR44-TL0_S0 | 1-BK-1_TS-1_TR44-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
106 | PCU01.INV6-BK-1_TS-1_TR44-TL0_S1 | 1-BK-1_TS-1_TR44-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
107 | PCU01.INV6-BK-1_TS-1_TR45-TL0_S0 | 1-BK-1_TS-1_TR45-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
108 | PCU01.INV6-BK-1_TS-1_TR45-TL0_S1 | 1-BK-1_TS-1_TR45-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
109 | PCU01.INV7-BK-1_TS-2_TR0-TL0_S0 | 1-BK-1_TS-2_TR0-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
110 | PCU01.INV7-BK-1_TS-2_TR0-TL0_S1 | 1-BK-1_TS-2_TR0-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
111 | PCU01.INV7-BK-1_TS-2_TR1-TL0_S0 | 1-BK-1_TS-2_TR1-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
112 | PCU01.INV7-BK-1_TS-2_TR1-TL0_S1 | 1-BK-1_TS-2_TR1-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
113 | PCU01.INV7-BK-1_TS-2_TR2-TL0_S0 | 1-BK-1_TS-2_TR2-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
114 | PCU01.INV7-BK-1_TS-2_TR2-TL0_S1 | 1-BK-1_TS-2_TR2-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
115 | PCU01.INV7-BK-1_TS-2_TR3-TL0_S0 | 1-BK-1_TS-2_TR3-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
116 | PCU01.INV7-BK-1_TS-2_TR3-TL0_S1 | 1-BK-1_TS-2_TR3-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
117 | PCU01.INV7-BK-1_TS-2_TR4-TL0_S0 | 1-BK-1_TS-2_TR4-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
118 | PCU01.INV7-BK-1_TS-2_TR4-TL0_S1 | 1-BK-1_TS-2_TR4-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
119 | PCU01.INV7-BK-1_TS-2_TR5-TL0_S0 | 1-BK-1_TS-2_TR5-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
120 | PCU01.INV7-BK-1_TS-2_TR5-TL0_S1 | 1-BK-1_TS-2_TR5-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
121 | PCU01.INV7-BK-1_TS-2_TR6-TL0_S0 | 1-BK-1_TS-2_TR6-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
122 | PCU01.INV7-BK-1_TS-2_TR6-TL0_S1 | 1-BK-1_TS-2_TR6-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
123 | PCU01.INV7-BK-1_TS-2_TR7-TL0_S0 | 1-BK-1_TS-2_TR7-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
124 | PCU01.INV7-BK-1_TS-2_TR7-TL0_S1 | 1-BK-1_TS-2_TR7-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
125 | PCU01.INV7-BK-1_TS-2_TR8-TL0_S0 | 1-BK-1_TS-2_TR8-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
126 | PCU01.INV7-BK-1_TS-2_TR8-TL0_S1 | 1-BK-1_TS-2_TR8-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
127 | PCU01.INV7-BK-1_TS-2_TR9-TL0_S0 | 1-BK-1_TS-2_TR9-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
128 | PCU01.INV7-BK-1_TS-2_TR9-TL0_S1 | 1-BK-1_TS-2_TR9-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
129 | PCU01.INV7-BK-1_TS-2_TR10-TL0_S0 | 1-BK-1_TS-2_TR10-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
130 | PCU01.INV7-BK-1_TS-2_TR10-TL0_S1 | 1-BK-1_TS-2_TR10-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
131 | PCU01.INV8-BK-1_TS-2_TR11-TL0_S0 | 1-BK-1_TS-2_TR11-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
132 | PCU01.INV8-BK-1_TS-2_TR11-TL0_S1 | 1-BK-1_TS-2_TR11-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
133 | PCU01.INV8-BK-1_TS-2_TR12-TL0_S0 | 1-BK-1_TS-2_TR12-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
134 | PCU01.INV8-BK-1_TS-2_TR12-TL0_S1 | 1-BK-1_TS-2_TR12-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
135 | PCU01.INV8-BK-1_TS-2_TR13-TL0_S0 | 1-BK-1_TS-2_TR13-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
136 | PCU01.INV8-BK-1_TS-2_TR13-TL0_S1 | 1-BK-1_TS-2_TR13-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
137 | PCU01.INV8-BK-1_TS-2_TR14-TL0_S0 | 1-BK-1_TS-2_TR14-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
138 | PCU01.INV8-BK-1_TS-2_TR14-TL0_S1 | 1-BK-1_TS-2_TR14-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
139 | PCU01.INV8-BK-1_TS-2_TR15-TL0_S0 | 1-BK-1_TS-2_TR15-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
140 | PCU01.INV8-BK-1_TS-2_TR15-TL0_S1 | 1-BK-1_TS-2_TR15-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
141 | PCU01.INV8-BK-1_TS-2_TR16-TL0_S0 | 1-BK-1_TS-2_TR16-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
142 | PCU01.INV8-BK-1_TS-2_TR16-TL0_S1 | 1-BK-1_TS-2_TR16-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
143 | PCU01.INV8-BK-1_TS-2_TR17-TL0_S0 | 1-BK-1_TS-2_TR17-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
144 | PCU01.INV8-BK-1_TS-2_TR17-TL0_S1 | 1-BK-1_TS-2_TR17-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
145 | PCU01.INV8-BK-1_TS-2_TR18-TL0_S0 | 1-BK-1_TS-2_TR18-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
146 | PCU01.INV8-BK-1_TS-2_TR18-TL0_S1 | 1-BK-1_TS-2_TR18-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
147 | PCU01.INV8-BK-1_TS-2_TR19-TL0_S0 | 1-BK-1_TS-2_TR19-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
148 | PCU01.INV8-BK-1_TS-2_TR19-TL0_S1 | 1-BK-1_TS-2_TR19-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
149 | PCU01.INV8-BK-1_TS-2_TR20-TL0_S0 | 1-BK-1_TS-2_TR20-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
150 | PCU01.INV8-BK-1_TS-2_TR20-TL0_S1 | 1-BK-1_TS-2_TR20-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
151 | PCU01.INV8-BK-1_TS-2_TR21-TL0_S0 | 1-BK-1_TS-2_TR21-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
152 | PCU01.INV8-BK-1_TS-2_TR21-TL0_S1 | 1-BK-1_TS-2_TR21-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
153 | PCU01.INV9-BK-1_TS-2_TR22-TL0_S0 | 1-BK-1_TS-2_TR22-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
154 | PCU01.INV9-BK-1_TS-2_TR22-TL0_S1 | 1-BK-1_TS-2_TR22-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
155 | PCU01.INV9-BK-1_TS-2_TR23-TL0_S0 | 1-BK-1_TS-2_TR23-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
156 | PCU01.INV9-BK-1_TS-2_TR23-TL0_S1 | 1-BK-1_TS-2_TR23-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
157 | PCU01.INV9-BK-1_TS-2_TR24-TL0_S0 | 1-BK-1_TS-2_TR24-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
158 | PCU01.INV9-BK-1_TS-2_TR24-TL0_S1 | 1-BK-1_TS-2_TR24-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
159 | PCU01.INV9-BK-1_TS-2_TR25-TL0_S0 | 1-BK-1_TS-2_TR25-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
160 | PCU01.INV9-BK-1_TS-2_TR25-TL0_S1 | 1-BK-1_TS-2_TR25-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
161 | PCU01.INV9-BK-1_TS-2_TR26-TL0_S0 | 1-BK-1_TS-2_TR26-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
162 | PCU01.INV9-BK-1_TS-2_TR26-TL0_S1 | 1-BK-1_TS-2_TR26-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
163 | PCU01.INV9-BK-1_TS-2_TR27-TL0_S0 | 1-BK-1_TS-2_TR27-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
164 | PCU01.INV9-BK-1_TS-2_TR27-TL0_S1 | 1-BK-1_TS-2_TR27-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
165 | PCU01.INV9-BK-1_TS-2_TR28-TL0_S0 | 1-BK-1_TS-2_TR28-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
166 | PCU01.INV9-BK-1_TS-2_TR28-TL0_S1 | 1-BK-1_TS-2_TR28-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
167 | PCU01.INV9-BK-1_TS-2_TR29-TL0_S0 | 1-BK-1_TS-2_TR29-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
168 | PCU01.INV9-BK-1_TS-2_TR29-TL0_S1 | 1-BK-1_TS-2_TR29-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
169 | PCU01.INV9-BK-1_TS-2_TR30-TL0_S0 | 1-BK-1_TS-2_TR30-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
170 | PCU01.INV9-BK-1_TS-2_TR30-TL0_S1 | 1-BK-1_TS-2_TR30-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
171 | PCU01.INV9-BK-1_TS-2_TR31-TL0_S0 | 1-BK-1_TS-2_TR31-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
172 | PCU01.INV9-BK-1_TS-2_TR31-TL0_S1 | 1-BK-1_TS-2_TR31-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
173 | PCU01.INV9-BK-1_TS-2_TR32-TL0_S0 | 1-BK-1_TS-2_TR32-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
174 | PCU01.INV9-BK-1_TS-2_TR32-TL0_S1 | 1-BK-1_TS-2_TR32-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
175 | PCU01.INV10-BK-1_TS-2_TR33-TL0_S0 | 1-BK-1_TS-2_TR33-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
176 | PCU01.INV10-BK-1_TS-2_TR33-TL0_S1 | 1-BK-1_TS-2_TR33-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
177 | PCU01.INV10-BK-1_TS-2_TR34-TL0_S0 | 1-BK-1_TS-2_TR34-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
178 | PCU01.INV10-BK-1_TS-2_TR34-TL0_S1 | 1-BK-1_TS-2_TR34-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
179 | PCU01.INV10-BK-1_TS-2_TR35-TL0_S0 | 1-BK-1_TS-2_TR35-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
180 | PCU01.INV10-BK-1_TS-2_TR35-TL0_S1 | 1-BK-1_TS-2_TR35-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
181 | PCU01.INV10-BK-1_TS-2_TR36-TL0_S0 | 1-BK-1_TS-2_TR36-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
182 | PCU01.INV10-BK-1_TS-2_TR36-TL0_S1 | 1-BK-1_TS-2_TR36-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
183 | PCU01.INV10-BK-1_TS-2_TR37-TL0_S0 | 1-BK-1_TS-2_TR37-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
184 | PCU01.INV10-BK-1_TS-2_TR37-TL0_S1 | 1-BK-1_TS-2_TR37-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
185 | PCU01.INV10-BK-1_TS-2_TR38-TL0_S0 | 1-BK-1_TS-2_TR38-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
186 | PCU01.INV10-BK-1_TS-2_TR38-TL0_S1 | 1-BK-1_TS-2_TR38-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
187 | PCU01.INV10-BK-1_TS-2_TR39-TL0_S0 | 1-BK-1_TS-2_TR39-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
188 | PCU01.INV10-BK-1_TS-2_TR39-TL0_S1 | 1-BK-1_TS-2_TR39-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
189 | PCU01.INV10-BK-1_TS-2_TR40-TL0_S0 | 1-BK-1_TS-2_TR40-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
190 | PCU01.INV10-BK-1_TS-2_TR40-TL0_S1 | 1-BK-1_TS-2_TR40-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
191 | PCU01.INV10-BK-1_TS-2_TR41-TL0_S0 | 1-BK-1_TS-2_TR41-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
192 | PCU01.INV10-BK-1_TS-2_TR41-TL0_S1 | 1-BK-1_TS-2_TR41-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
193 | PCU01.INV10-BK-1_TS-2_TR42-TL0_S0 | 1-BK-1_TS-2_TR42-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
194 | PCU01.INV10-BK-1_TS-2_TR42-TL0_S1 | 1-BK-1_TS-2_TR42-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
195 | PCU01.INV10-BK-1_TS-2_TR43-TL0_S0 | 1-BK-1_TS-2_TR43-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
196 | PCU01.INV10-BK-1_TS-2_TR43-TL0_S1 | 1-BK-1_TS-2_TR43-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
197 | PCU01.INV11-BK-1_TS-3_TR0-TL0_S0 | 1-BK-1_TS-3_TR0-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
198 | PCU01.INV11-BK-1_TS-3_TR0-TL0_S1 | 1-BK-1_TS-3_TR0-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
199 | PCU01.INV11-BK-1_TS-3_TR1-TL0_S0 | 1-BK-1_TS-3_TR1-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
200 | PCU01.INV11-BK-1_TS-3_TR1-TL0_S1 | 1-BK-1_TS-3_TR1-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
201 | PCU01.INV11-BK-1_TS-3_TR2-TL0_S0 | 1-BK-1_TS-3_TR2-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
202 | PCU01.INV11-BK-1_TS-3_TR2-TL0_S1 | 1-BK-1_TS-3_TR2-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
203 | PCU01.INV11-BK-1_TS-3_TR3-TL0_S0 | 1-BK-1_TS-3_TR3-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
204 | PCU01.INV11-BK-1_TS-3_TR3-TL0_S1 | 1-BK-1_TS-3_TR3-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
205 | PCU01.INV11-BK-1_TS-3_TR4-TL0_S0 | 1-BK-1_TS-3_TR4-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
206 | PCU01.INV11-BK-1_TS-3_TR4-TL0_S1 | 1-BK-1_TS-3_TR4-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
207 | PCU01.INV11-BK-1_TS-3_TR5-TL0_S0 | 1-BK-1_TS-3_TR5-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
208 | PCU01.INV11-BK-1_TS-3_TR5-TL0_S1 | 1-BK-1_TS-3_TR5-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
209 | PCU01.INV11-BK-1_TS-3_TR6-TL0_S0 | 1-BK-1_TS-3_TR6-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
210 | PCU01.INV11-BK-1_TS-3_TR6-TL0_S1 | 1-BK-1_TS-3_TR6-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
211 | PCU01.INV11-BK-1_TS-3_TR7-TL0_S0 | 1-BK-1_TS-3_TR7-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
212 | PCU01.INV11-BK-1_TS-3_TR7-TL0_S1 | 1-BK-1_TS-3_TR7-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
213 | PCU01.INV11-BK-1_TS-3_TR8-TL0_S0 | 1-BK-1_TS-3_TR8-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
214 | PCU01.INV11-BK-1_TS-3_TR8-TL0_S1 | 1-BK-1_TS-3_TR8-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
215 | PCU01.INV11-BK-1_TS-3_TR9-TL0_S0 | 1-BK-1_TS-3_TR9-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
216 | PCU01.INV11-BK-1_TS-3_TR9-TL0_S1 | 1-BK-1_TS-3_TR9-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
217 | PCU01.INV12-BK-1_TS-3_TR10-TL0_S0 | 1-BK-1_TS-3_TR10-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
218 | PCU01.INV12-BK-1_TS-3_TR10-TL0_S1 | 1-BK-1_TS-3_TR10-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
219 | PCU01.INV12-BK-1_TS-3_TR11-TL0_S0 | 1-BK-1_TS-3_TR11-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
220 | PCU01.INV12-BK-1_TS-3_TR11-TL0_S1 | 1-BK-1_TS-3_TR11-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
221 | PCU01.INV12-BK-1_TS-3_TR12-TL0_S0 | 1-BK-1_TS-3_TR12-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
222 | PCU01.INV12-BK-1_TS-3_TR12-TL0_S1 | 1-BK-1_TS-3_TR12-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
223 | PCU01.INV12-BK-1_TS-3_TR13-TL0_S0 | 1-BK-1_TS-3_TR13-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
224 | PCU01.INV12-BK-1_TS-3_TR13-TL0_S1 | 1-BK-1_TS-3_TR13-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
225 | PCU01.INV12-BK-1_TS-3_TR14-TL0_S0 | 1-BK-1_TS-3_TR14-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
226 | PCU01.INV12-BK-1_TS-3_TR14-TL0_S1 | 1-BK-1_TS-3_TR14-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
227 | PCU01.INV12-BK-1_TS-3_TR15-TL0_S0 | 1-BK-1_TS-3_TR15-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
228 | PCU01.INV12-BK-1_TS-3_TR15-TL0_S1 | 1-BK-1_TS-3_TR15-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
229 | PCU01.INV12-BK-1_TS-3_TR16-TL0_S0 | 1-BK-1_TS-3_TR16-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
230 | PCU01.INV12-BK-1_TS-3_TR16-TL0_S1 | 1-BK-1_TS-3_TR16-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
231 | PCU01.INV12-BK-1_TS-3_TR17-TL0_S0 | 1-BK-1_TS-3_TR17-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
232 | PCU01.INV12-BK-1_TS-3_TR17-TL0_S1 | 1-BK-1_TS-3_TR17-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
233 | PCU01.INV12-BK-1_TS-3_TR18-TL0_S0 | 1-BK-1_TS-3_TR18-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
234 | PCU01.INV12-BK-1_TS-3_TR18-TL0_S1 | 1-BK-1_TS-3_TR18-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
235 | PCU01.INV12-BK-1_TS-3_TR19-TL0_S0 | 1-BK-1_TS-3_TR19-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
236 | PCU01.INV12-BK-1_TS-3_TR19-TL0_S1 | 1-BK-1_TS-3_TR19-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
237 | PCU01.INV13-BK-1_TS-3_TR20-TL0_S0 | 1-BK-1_TS-3_TR20-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
238 | PCU01.INV13-BK-1_TS-3_TR20-TL0_S1 | 1-BK-1_TS-3_TR20-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
239 | PCU01.INV13-BK-1_TS-3_TR21-TL0_S0 | 1-BK-1_TS-3_TR21-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
240 | PCU01.INV13-BK-1_TS-3_TR21-TL0_S1 | 1-BK-1_TS-3_TR21-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
241 | PCU01.INV13-BK-1_TS-3_TR22-TL0_S0 | 1-BK-1_TS-3_TR22-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
242 | PCU01.INV13-BK-1_TS-3_TR22-TL0_S1 | 1-BK-1_TS-3_TR22-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
243 | PCU01.INV13-BK-1_TS-3_TR23-TL0_S0 | 1-BK-1_TS-3_TR23-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
244 | PCU01.INV13-BK-1_TS-3_TR23-TL0_S1 | 1-BK-1_TS-3_TR23-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
245 | PCU01.INV13-BK-1_TS-3_TR24-TL0_S0 | 1-BK-1_TS-3_TR24-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
246 | PCU01.INV13-BK-1_TS-3_TR24-TL0_S1 | 1-BK-1_TS-3_TR24-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
247 | PCU01.INV13-BK-1_TS-3_TR25-TL0_S0 | 1-BK-1_TS-3_TR25-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
248 | PCU01.INV13-BK-1_TS-3_TR25-TL0_S1 | 1-BK-1_TS-3_TR25-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
249 | PCU01.INV13-BK-1_TS-3_TR26-TL0_S0 | 1-BK-1_TS-3_TR26-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
250 | PCU01.INV13-BK-1_TS-3_TR26-TL0_S1 | 1-BK-1_TS-3_TR26-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
251 | PCU01.INV13-BK-1_TS-3_TR27-TL0_S0 | 1-BK-1_TS-3_TR27-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
252 | PCU01.INV13-BK-1_TS-3_TR27-TL0_S1 | 1-BK-1_TS-3_TR27-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
253 | PCU01.INV13-BK-1_TS-3_TR28-TL0_S0 | 1-BK-1_TS-3_TR28-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
254 | PCU01.INV13-BK-1_TS-3_TR28-TL0_S1 | 1-BK-1_TS-3_TR28-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
255 | PCU01.INV13-BK-1_TS-3_TR29-TL0_S0 | 1-BK-1_TS-3_TR29-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
256 | PCU01.INV13-BK-1_TS-3_TR29-TL0_S1 | 1-BK-1_TS-3_TR29-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
257 | PCU01.INV14-BK-1_TS-3_TR30-TL0_S0 | 1-BK-1_TS-3_TR30-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
258 | PCU01.INV14-BK-1_TS-3_TR30-TL0_S1 | 1-BK-1_TS-3_TR30-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
259 | PCU01.INV14-BK-1_TS-3_TR31-TL0_S0 | 1-BK-1_TS-3_TR31-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
260 | PCU01.INV14-BK-1_TS-3_TR31-TL0_S1 | 1-BK-1_TS-3_TR31-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
261 | PCU01.INV14-BK-1_TS-3_TR32-TL0_S0 | 1-BK-1_TS-3_TR32-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
262 | PCU01.INV14-BK-1_TS-3_TR32-TL0_S1 | 1-BK-1_TS-3_TR32-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
263 | PCU01.INV14-BK-1_TS-3_TR33-TL0_S0 | 1-BK-1_TS-3_TR33-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
264 | PCU01.INV14-BK-1_TS-3_TR33-TL0_S1 | 1-BK-1_TS-3_TR33-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
265 | PCU01.INV14-BK-1_TS-3_TR34-TL0_S0 | 1-BK-1_TS-3_TR34-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
266 | PCU01.INV14-BK-1_TS-3_TR34-TL0_S1 | 1-BK-1_TS-3_TR34-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
267 | PCU01.INV14-BK-1_TS-3_TR35-TL0_S0 | 1-BK-1_TS-3_TR35-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
268 | PCU01.INV14-BK-1_TS-3_TR35-TL0_S1 | 1-BK-1_TS-3_TR35-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
269 | PCU01.INV14-BK-1_TS-3_TR36-TL0_S0 | 1-BK-1_TS-3_TR36-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
270 | PCU01.INV14-BK-1_TS-3_TR36-TL0_S1 | 1-BK-1_TS-3_TR36-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
271 | PCU01.INV14-BK-1_TS-3_TR37-TL0_S0 | 1-BK-1_TS-3_TR37-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
272 | PCU01.INV14-BK-1_TS-3_TR37-TL0_S1 | 1-BK-1_TS-3_TR37-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
273 | PCU01.INV14-BK-1_TS-3_TR38-TL0_S0 | 1-BK-1_TS-3_TR38-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
274 | PCU01.INV14-BK-1_TS-3_TR38-TL0_S1 | 1-BK-1_TS-3_TR38-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
275 | PCU01.INV14-BK-1_TS-3_TR39-TL0_S1 | 1-BK-1_TS-3_TR39-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
276 | PCU01.INV15-BK-1_TS-3_TR39-TL0_S0 | 1-BK-1_TS-3_TR39-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
277 | PCU01.INV15-BK-1_TS-3_TR40-TL0_S0 | 1-BK-1_TS-3_TR40-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
278 | PCU01.INV15-BK-1_TS-3_TR40-TL0_S1 | 1-BK-1_TS-3_TR40-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
279 | PCU01.INV15-BK-1_TS-3_TR41-TL0_S0 | 1-BK-1_TS-3_TR41-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
280 | PCU01.INV15-BK-1_TS-3_TR41-TL0_S1 | 1-BK-1_TS-3_TR41-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
281 | PCU01.INV15-BK-1_TS-3_TR42-TL0_S0 | 1-BK-1_TS-3_TR42-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
282 | PCU01.INV15-BK-1_TS-3_TR42-TL0_S1 | 1-BK-1_TS-3_TR42-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
283 | PCU01.INV15-BK-1_TS-3_TR43-TL0_S0 | 1-BK-1_TS-3_TR43-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
284 | PCU01.INV15-BK-1_TS-3_TR43-TL0_S1 | 1-BK-1_TS-3_TR43-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
285 | PCU01.INV15-BK-1_TS-3_TR44-TL0_S0 | 1-BK-1_TS-3_TR44-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
286 | PCU01.INV15-BK-1_TS-3_TR44-TL0_S1 | 1-BK-1_TS-3_TR44-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
287 | PCU01.INV15-BK-1_TS-3_TR45-TL0_S0 | 1-BK-1_TS-3_TR45-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
288 | PCU01.INV15-BK-1_TS-3_TR45-TL0_S1 | 1-BK-1_TS-3_TR45-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
289 | PCU01.INV15-BK-1_TS-3_TR46-TL0_S0 | 1-BK-1_TS-3_TR46-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
290 | PCU01.INV15-BK-1_TS-3_TR46-TL0_S1 | 1-BK-1_TS-3_TR46-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
291 | PCU01.INV15-BK-1_TS-3_TR47-TL0_S0 | 1-BK-1_TS-3_TR47-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
292 | PCU01.INV15-BK-1_TS-3_TR47-TL0_S1 | 1-BK-1_TS-3_TR47-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
293 | PCU01.INV15-BK-1_TS-3_TR48-TL0_S0 | 1-BK-1_TS-3_TR48-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
294 | PCU01.INV15-BK-1_TS-3_TR48-TL0_S1 | 1-BK-1_TS-3_TR48-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
295 | PCU01.INV16-BK-1_TN-1_TR0-TL0_S0 | 1-BK-1_TN-1_TR0-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
296 | PCU01.INV16-BK-1_TN-1_TR0-TL0_S1 | 1-BK-1_TN-1_TR0-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
297 | PCU01.INV16-BK-1_TN-1_TR1-TL0_S0 | 1-BK-1_TN-1_TR1-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
298 | PCU01.INV16-BK-1_TN-1_TR1-TL0_S1 | 1-BK-1_TN-1_TR1-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
299 | PCU01.INV16-BK-1_TN-1_TR2-TL0_S0 | 1-BK-1_TN-1_TR2-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
300 | PCU01.INV16-BK-1_TN-1_TR2-TL0_S1 | 1-BK-1_TN-1_TR2-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
301 | PCU01.INV16-BK-1_TN-1_TR3-TL0_S0 | 1-BK-1_TN-1_TR3-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
302 | PCU01.INV16-BK-1_TN-1_TR3-TL0_S1 | 1-BK-1_TN-1_TR3-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
303 | PCU01.INV16-BK-1_TN-1_TR4-TL0_S0 | 1-BK-1_TN-1_TR4-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
304 | PCU01.INV16-BK-1_TN-1_TR4-TL0_S1 | 1-BK-1_TN-1_TR4-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
305 | PCU01.INV16-BK-1_TN-1_TR5-TL0_S0 | 1-BK-1_TN-1_TR5-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
306 | PCU01.INV16-BK-1_TN-1_TR5-TL0_S1 | 1-BK-1_TN-1_TR5-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
307 | PCU01.INV16-BK-1_TN-1_TR6-TL0_S0 | 1-BK-1_TN-1_TR6-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
308 | PCU01.INV16-BK-1_TN-1_TR6-TL0_S1 | 1-BK-1_TN-1_TR6-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
309 | PCU01.INV16-BK-1_TN-1_TR7-TL0_S0 | 1-BK-1_TN-1_TR7-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
310 | PCU01.INV16-BK-1_TN-1_TR7-TL0_S1 | 1-BK-1_TN-1_TR7-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
311 | PCU01.INV16-BK-1_TN-1_TR8-TL0_S0 | 1-BK-1_TN-1_TR8-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
312 | PCU01.INV16-BK-1_TN-1_TR8-TL0_S1 | 1-BK-1_TN-1_TR8-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
313 | PCU01.INV16-BK-1_TN-1_TR9-TL0_S0 | 1-BK-1_TN-1_TR9-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
314 | PCU01.INV16-BK-1_TN-1_TR9-TL0_S1 | 1-BK-1_TN-1_TR9-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
315 | PCU01.INV16-BK-1_TN-1_TR10-TL0_S0 | 1-BK-1_TN-1_TR10-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
316 | PCU01.INV17-BK-1_TN-1_TR10-TL0_S1 | 1-BK-1_TN-1_TR10-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
317 | PCU01.INV17-BK-1_TN-1_TR11-TL0_S0 | 1-BK-1_TN-1_TR11-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
318 | PCU01.INV17-BK-1_TN-1_TR11-TL0_S1 | 1-BK-1_TN-1_TR11-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
319 | PCU01.INV17-BK-1_TN-1_TR12-TL0_S0 | 1-BK-1_TN-1_TR12-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
320 | PCU01.INV17-BK-1_TN-1_TR12-TL0_S1 | 1-BK-1_TN-1_TR12-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
321 | PCU01.INV17-BK-1_TN-1_TR13-TL0_S0 | 1-BK-1_TN-1_TR13-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
322 | PCU01.INV17-BK-1_TN-1_TR13-TL0_S1 | 1-BK-1_TN-1_TR13-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
323 | PCU01.INV17-BK-1_TN-1_TR14-TL0_S0 | 1-BK-1_TN-1_TR14-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
324 | PCU01.INV17-BK-1_TN-1_TR14-TL0_S1 | 1-BK-1_TN-1_TR14-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
325 | PCU01.INV17-BK-1_TN-1_TR15-TL0_S0 | 1-BK-1_TN-1_TR15-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
326 | PCU01.INV17-BK-1_TN-1_TR15-TL0_S1 | 1-BK-1_TN-1_TR15-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
327 | PCU01.INV17-BK-1_TN-1_TR16-TL0_S0 | 1-BK-1_TN-1_TR16-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
328 | PCU01.INV17-BK-1_TN-1_TR16-TL0_S1 | 1-BK-1_TN-1_TR16-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
329 | PCU01.INV17-BK-1_TN-1_TR17-TL0_S0 | 1-BK-1_TN-1_TR17-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
330 | PCU01.INV17-BK-1_TN-1_TR17-TL0_S1 | 1-BK-1_TN-1_TR17-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
331 | PCU01.INV17-BK-1_TN-1_TR18-TL0_S0 | 1-BK-1_TN-1_TR18-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
332 | PCU01.INV17-BK-1_TN-1_TR18-TL0_S1 | 1-BK-1_TN-1_TR18-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
333 | PCU01.INV17-BK-1_TN-1_TR19-TL0_S0 | 1-BK-1_TN-1_TR19-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
334 | PCU01.INV17-BK-1_TN-1_TR19-TL0_S1 | 1-BK-1_TN-1_TR19-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
335 | PCU01.INV17-BK-1_TN-1_TR20-TL0_S0 | 1-BK-1_TN-1_TR20-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
336 | PCU01.INV17-BK-1_TN-1_TR20-TL0_S1 | 1-BK-1_TN-1_TR20-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
337 | PCU01.INV18-BK-1_TN-2_TR0-TL0_S0 | 1-BK-1_TN-2_TR0-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
338 | PCU01.INV18-BK-1_TN-2_TR0-TL0_S1 | 1-BK-1_TN-2_TR0-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
339 | PCU01.INV18-BK-1_TN-2_TR1-TL0_S0 | 1-BK-1_TN-2_TR1-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
340 | PCU01.INV18-BK-1_TN-2_TR1-TL0_S1 | 1-BK-1_TN-2_TR1-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
341 | PCU01.INV18-BK-1_TN-2_TR2-TL0_S0 | 1-BK-1_TN-2_TR2-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
342 | PCU01.INV18-BK-1_TN-2_TR2-TL0_S1 | 1-BK-1_TN-2_TR2-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
343 | PCU01.INV18-BK-1_TN-2_TR3-TL0_S0 | 1-BK-1_TN-2_TR3-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
344 | PCU01.INV18-BK-1_TN-2_TR3-TL0_S1 | 1-BK-1_TN-2_TR3-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
345 | PCU01.INV18-BK-1_TN-2_TR4-TL0_S0 | 1-BK-1_TN-2_TR4-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
346 | PCU01.INV18-BK-1_TN-2_TR4-TL0_S1 | 1-BK-1_TN-2_TR4-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
347 | PCU01.INV18-BK-1_TN-2_TR5-TL0_S0 | 1-BK-1_TN-2_TR5-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
348 | PCU01.INV18-BK-1_TN-2_TR5-TL0_S1 | 1-BK-1_TN-2_TR5-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
349 | PCU01.INV18-BK-1_TN-2_TR6-TL0_S0 | 1-BK-1_TN-2_TR6-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
350 | PCU01.INV18-BK-1_TN-2_TR6-TL0_S1 | 1-BK-1_TN-2_TR6-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
351 | PCU01.INV18-BK-1_TN-2_TR7-TL0_S0 | 1-BK-1_TN-2_TR7-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
352 | PCU01.INV18-BK-1_TN-2_TR7-TL0_S1 | 1-BK-1_TN-2_TR7-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
353 | PCU01.INV18-BK-1_TN-2_TR8-TL0_S0 | 1-BK-1_TN-2_TR8-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
354 | PCU01.INV18-BK-1_TN-2_TR8-TL0_S1 | 1-BK-1_TN-2_TR8-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
355 | PCU01.INV18-BK-1_TN-2_TR9-TL0_S0 | 1-BK-1_TN-2_TR9-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
356 | PCU01.INV18-BK-1_TN-2_TR9-TL0_S1 | 1-BK-1_TN-2_TR9-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
357 | PCU01.INV18-BK-1_TN-2_TR10-TL0_S0 | 1-BK-1_TN-2_TR10-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
358 | PCU01.INV19-BK-1_TN-0_TR0-TL0_S0 | 1-BK-1_TN-0_TR0-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 174.83 | 87.41 | 87.41 | 11.28 | 1061.2 | 17.31 | 0 | 13.08 | 13.08 | 1.23 | 226.44 | 1.23
359 | PCU01.INV19-BK-1_TN-0_TR0-TL0_S1 | 1-BK-1_TN-0_TR0-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 100 | 50 | 50 | 11.28 | 1061.2 | 17.31 | 0 | 7.48 | 7.48 | 0.71 | 129.52 | 0.71
360 | PCU01.INV19-BK-1_TN-0_TR1-TL0_S0 | 1-BK-1_TN-0_TR1-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 164.73 | 82.36 | 82.36 | 6.28 | 1061.2 | 17.31 | 0 | 12.33 | 12.33 | 1.16 | 213.35 | 1.16
361 | PCU01.INV19-BK-1_TN-0_TR1-TL0_S1 | 1-BK-1_TN-0_TR1-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 89.9 | 44.95 | 44.95 | 6.28 | 1061.2 | 17.31 | 0 | 6.73 | 6.73 | 0.63 | 116.43 | 0.63
362 | PCU01.INV19-BK-1_TN-0_TR2-TL0_S0 | 1-BK-1_TN-0_TR2-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 174.83 | 87.41 | 87.41 | 11.28 | 1061.2 | 17.31 | 0 | 13.08 | 13.08 | 1.23 | 226.44 | 1.23
363 | PCU01.INV19-BK-1_TN-0_TR2-TL0_S1 | 1-BK-1_TN-0_TR2-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 100 | 50 | 50 | 11.28 | 1061.2 | 17.31 | 0 | 7.48 | 7.48 | 0.71 | 129.52 | 0.71
364 | PCU01.INV19-BK-1_TN-0_TR3-TL0_S0 | 1-BK-1_TN-0_TR3-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 184.93 | 92.46 | 92.46 | 16.28 | 1061.2 | 17.31 | 0 | 13.84 | 13.84 | 1.3 | 239.52 | 1.31
365 | PCU01.INV19-BK-1_TN-0_TR3-TL0_S1 | 1-BK-1_TN-0_TR3-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 110.1 | 55.05 | 55.05 | 16.28 | 1061.2 | 17.31 | 0 | 8.24 | 8.24 | 0.78 | 142.6 | 0.78
366 | PCU01.INV19-BK-1_TN-0_TR4-TL0_S0 | 1-BK-1_TN-0_TR4-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 195.03 | 97.51 | 97.51 | 21.28 | 1061.2 | 17.31 | 0 | 14.59 | 14.59 | 1.38 | 252.6 | 1.38
367 | PCU01.INV19-BK-1_TN-0_TR4-TL0_S1 | 1-BK-1_TN-0_TR4-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 120.2 | 60.1 | 60.1 | 21.28 | 1061.2 | 17.31 | 0 | 8.99 | 8.99 | 0.85 | 155.68 | 0.85
368 | PCU01.INV19-BK-1_TN-0_TR5-TL0_S0 | 1-BK-1_TN-0_TR5-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 205.13 | 102.56 | 102.56 | 26.28 | 1061.2 | 17.31 | 0 | 15.35 | 15.35 | 1.45 | 265.68 | 1.45
369 | PCU01.INV19-BK-1_TN-0_TR5-TL0_S1 | 1-BK-1_TN-0_TR5-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 130.3 | 65.15 | 65.15 | 26.28 | 1061.2 | 17.31 | 0 | 9.75 | 9.75 | 0.92 | 168.76 | 0.92
370 | PCU01.INV19-BK-1_TN-1_TR21-TL0_S0 | 1-BK-1_TN-1_TR21-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
371 | PCU01.INV19-BK-1_TN-1_TR21-TL0_S1 | 1-BK-1_TN-1_TR21-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
372 | PCU01.INV19-BK-1_TN-1_TR22-TL0_S0 | 1-BK-1_TN-1_TR22-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
373 | PCU01.INV19-BK-1_TN-1_TR22-TL0_S1 | 1-BK-1_TN-1_TR22-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
374 | PCU01.INV19-BK-1_TN-1_TR23-TL0_S0 | 1-BK-1_TN-1_TR23-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
375 | PCU01.INV19-BK-1_TN-1_TR23-TL0_S1 | 1-BK-1_TN-1_TR23-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
376 | PCU01.INV19-BK-1_TN-1_TR24-TL0_S0 | 1-BK-1_TN-1_TR24-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
377 | PCU01.INV19-BK-1_TN-1_TR24-TL0_S1 | 1-BK-1_TN-1_TR24-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
378 | PCU01.INV19-BK-1_TN-1_TR25-TL0_S0 | 1-BK-1_TN-1_TR25-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
379 | PCU01.INV19-BK-1_TN-1_TR25-TL0_S1 | 1-BK-1_TN-1_TR25-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
380 | PCU01.INV20-BK-1_TN-1_TR26-TL0_S0 | 1-BK-1_TN-1_TR26-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 174.83 | 87.41 | 87.41 | 11.28 | 1061.2 | 17.31 | 0 | 13.08 | 13.08 | 1.23 | 226.44 | 1.23
381 | PCU01.INV20-BK-1_TN-1_TR26-TL0_S1 | 1-BK-1_TN-1_TR26-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 100 | 50 | 50 | 11.28 | 1061.2 | 17.31 | 0 | 7.48 | 7.48 | 0.71 | 129.52 | 0.71
382 | PCU01.INV20-BK-1_TN-1_TR27-TL0_S0 | 1-BK-1_TN-1_TR27-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 164.73 | 82.36 | 82.36 | 6.28 | 1061.2 | 17.31 | 0 | 12.33 | 12.33 | 1.16 | 213.35 | 1.16
383 | PCU01.INV20-BK-1_TN-1_TR27-TL0_S1 | 1-BK-1_TN-1_TR27-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 89.9 | 44.95 | 44.95 | 6.28 | 1061.2 | 17.31 | 0 | 6.73 | 6.73 | 0.63 | 116.43 | 0.63
384 | PCU01.INV20-BK-1_TN-1_TR28-TL0_S0 | 1-BK-1_TN-1_TR28-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 174.83 | 87.41 | 87.41 | 11.28 | 1061.2 | 17.31 | 0 | 13.08 | 13.08 | 1.23 | 226.44 | 1.23
385 | PCU01.INV20-BK-1_TN-1_TR28-TL0_S1 | 1-BK-1_TN-1_TR28-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 100 | 50 | 50 | 11.28 | 1061.2 | 17.31 | 0 | 7.48 | 7.48 | 0.71 | 129.52 | 0.71
386 | PCU01.INV20-BK-1_TN-1_TR29-TL0_S0 | 1-BK-1_TN-1_TR29-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 184.93 | 92.46 | 92.46 | 16.28 | 1061.2 | 17.31 | 0 | 13.84 | 13.84 | 1.3 | 239.52 | 1.31
387 | PCU01.INV20-BK-1_TN-1_TR29-TL0_S1 | 1-BK-1_TN-1_TR29-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 110.1 | 55.05 | 55.05 | 16.28 | 1061.2 | 17.31 | 0 | 8.24 | 8.24 | 0.78 | 142.6 | 0.78
388 | PCU01.INV20-BK-1_TN-1_TR30-TL0_S0 | 1-BK-1_TN-1_TR30-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 195.03 | 97.51 | 97.51 | 21.28 | 1061.2 | 17.31 | 0 | 14.59 | 14.59 | 1.38 | 252.6 | 1.38
389 | PCU01.INV20-BK-1_TN-1_TR30-TL0_S1 | 1-BK-1_TN-1_TR30-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 120.2 | 60.1 | 60.1 | 21.28 | 1061.2 | 17.31 | 0 | 8.99 | 8.99 | 0.85 | 155.68 | 0.85
390 | PCU01.INV20-BK-1_TN-2_TR10-TL0_S1 | 1-BK-1_TN-2_TR10-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
391 | PCU01.INV20-BK-1_TN-2_TR11-TL0_S0 | 1-BK-1_TN-2_TR11-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
392 | PCU01.INV20-BK-1_TN-2_TR11-TL0_S1 | 1-BK-1_TN-2_TR11-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
393 | PCU01.INV20-BK-1_TN-2_TR12-TL0_S0 | 1-BK-1_TN-2_TR12-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
394 | PCU01.INV20-BK-1_TN-2_TR12-TL0_S1 | 1-BK-1_TN-2_TR12-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
395 | PCU01.INV20-BK-1_TN-2_TR13-TL0_S0 | 1-BK-1_TN-2_TR13-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
396 | PCU01.INV20-BK-1_TN-2_TR13-TL0_S1 | 1-BK-1_TN-2_TR13-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
397 | PCU01.INV20-BK-1_TN-2_TR14-TL0_S0 | 1-BK-1_TN-2_TR14-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
398 | PCU01.INV20-BK-1_TN-2_TR14-TL0_S1 | 1-BK-1_TN-2_TR14-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
399 | PCU01.INV20-BK-1_TN-2_TR15-TL0_S0 | 1-BK-1_TN-2_TR15-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
400 | PCU01.INV20-BK-1_TN-2_TR15-TL0_S1 | 1-BK-1_TN-2_TR15-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 1 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
401 | PCU02.INV1-BK-2_TS-0_TR0-TL0_S0 | 2-BK-2_TS-0_TR0-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
402 | PCU02.INV1-BK-2_TS-0_TR0-TL0_S1 | 2-BK-2_TS-0_TR0-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
403 | PCU02.INV1-BK-2_TS-0_TR1-TL0_S0 | 2-BK-2_TS-0_TR1-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
404 | PCU02.INV1-BK-2_TS-0_TR1-TL0_S1 | 2-BK-2_TS-0_TR1-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
405 | PCU02.INV1-BK-2_TS-0_TR2-TL0_S0 | 2-BK-2_TS-0_TR2-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
406 | PCU02.INV1-BK-2_TS-0_TR2-TL0_S1 | 2-BK-2_TS-0_TR2-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
407 | PCU02.INV1-BK-2_TS-0_TR3-TL0_S0 | 2-BK-2_TS-0_TR3-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
408 | PCU02.INV1-BK-2_TS-0_TR3-TL0_S1 | 2-BK-2_TS-0_TR3-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
409 | PCU02.INV1-BK-2_TS-0_TR4-TL0_S0 | 2-BK-2_TS-0_TR4-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
410 | PCU02.INV1-BK-2_TS-0_TR4-TL0_S1 | 2-BK-2_TS-0_TR4-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
411 | PCU02.INV1-BK-2_TS-0_TR5-TL0_S0 | 2-BK-2_TS-0_TR5-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
412 | PCU02.INV1-BK-2_TS-0_TR5-TL0_S1 | 2-BK-2_TS-0_TR5-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
413 | PCU02.INV1-BK-2_TS-0_TR6-TL0_S0 | 2-BK-2_TS-0_TR6-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
414 | PCU02.INV1-BK-2_TS-0_TR6-TL0_S1 | 2-BK-2_TS-0_TR6-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
415 | PCU02.INV1-BK-2_TS-0_TR7-TL0_S0 | 2-BK-2_TS-0_TR7-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
416 | PCU02.INV1-BK-2_TS-0_TR7-TL0_S1 | 2-BK-2_TS-0_TR7-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
417 | PCU02.INV1-BK-2_TS-0_TR8-TL0_S0 | 2-BK-2_TS-0_TR8-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
418 | PCU02.INV1-BK-2_TS-0_TR8-TL0_S1 | 2-BK-2_TS-0_TR8-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
419 | PCU02.INV1-BK-2_TS-0_TR9-TL0_S0 | 2-BK-2_TS-0_TR9-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
420 | PCU02.INV1-BK-2_TS-0_TR9-TL0_S1 | 2-BK-2_TS-0_TR9-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
421 | PCU02.INV2-BK-2_TS-0_TR10-TL0_S0 | 2-BK-2_TS-0_TR10-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
422 | PCU02.INV2-BK-2_TS-0_TR10-TL0_S1 | 2-BK-2_TS-0_TR10-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
423 | PCU02.INV2-BK-2_TS-0_TR11-TL0_S0 | 2-BK-2_TS-0_TR11-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
424 | PCU02.INV2-BK-2_TS-0_TR11-TL0_S1 | 2-BK-2_TS-0_TR11-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
425 | PCU02.INV2-BK-2_TS-0_TR12-TL0_S0 | 2-BK-2_TS-0_TR12-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
426 | PCU02.INV2-BK-2_TS-0_TR12-TL0_S1 | 2-BK-2_TS-0_TR12-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
427 | PCU02.INV2-BK-2_TS-0_TR13-TL0_S0 | 2-BK-2_TS-0_TR13-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
428 | PCU02.INV2-BK-2_TS-0_TR13-TL0_S1 | 2-BK-2_TS-0_TR13-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
429 | PCU02.INV2-BK-2_TS-0_TR14-TL0_S0 | 2-BK-2_TS-0_TR14-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
430 | PCU02.INV2-BK-2_TS-0_TR14-TL0_S1 | 2-BK-2_TS-0_TR14-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
431 | PCU02.INV2-BK-2_TS-0_TR15-TL0_S0 | 2-BK-2_TS-0_TR15-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
432 | PCU02.INV2-BK-2_TS-0_TR15-TL0_S1 | 2-BK-2_TS-0_TR15-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
433 | PCU02.INV2-BK-2_TS-0_TR16-TL0_S0 | 2-BK-2_TS-0_TR16-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
434 | PCU02.INV2-BK-2_TS-0_TR16-TL0_S1 | 2-BK-2_TS-0_TR16-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
435 | PCU02.INV2-BK-2_TS-0_TR17-TL0_S0 | 2-BK-2_TS-0_TR17-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
436 | PCU02.INV2-BK-2_TS-0_TR17-TL0_S1 | 2-BK-2_TS-0_TR17-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
437 | PCU02.INV2-BK-2_TS-0_TR18-TL0_S0 | 2-BK-2_TS-0_TR18-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
438 | PCU02.INV2-BK-2_TS-0_TR18-TL0_S1 | 2-BK-2_TS-0_TR18-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
439 | PCU02.INV2-BK-2_TS-0_TR19-TL0_S0 | 2-BK-2_TS-0_TR19-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
440 | PCU02.INV2-BK-2_TS-0_TR19-TL0_S1 | 2-BK-2_TS-0_TR19-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
441 | PCU02.INV3-BK-2_TS-0_TR20-TL0_S0 | 2-BK-2_TS-0_TR20-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 159.06 | 79.53 | 79.53 | 37.5 | 1061.2 | 17.31 | 0 | 11.9 | 11.9 | 1.12 | 206.02 | 1.12
442 | PCU02.INV3-BK-2_TS-0_TR20-TL0_S1 | 2-BK-2_TS-0_TR20-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 84.23 | 42.12 | 42.12 | 37.5 | 1061.2 | 17.31 | 0 | 6.3 | 6.3 | 0.59 | 109.1 | 0.59
443 | PCU02.INV3-BK-2_TS-0_TR21-TL0_S0 | 2-BK-2_TS-0_TR21-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
444 | PCU02.INV3-BK-2_TS-0_TR21-TL0_S1 | 2-BK-2_TS-0_TR21-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
445 | PCU02.INV3-BK-2_TS-0_TR22-TL0_S0 | 2-BK-2_TS-0_TR22-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
446 | PCU02.INV3-BK-2_TS-0_TR22-TL0_S1 | 2-BK-2_TS-0_TR22-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
447 | PCU02.INV3-BK-2_TS-0_TR23-TL0_S0 | 2-BK-2_TS-0_TR23-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
448 | PCU02.INV3-BK-2_TS-0_TR23-TL0_S1 | 2-BK-2_TS-0_TR23-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
449 | PCU02.INV3-BK-2_TS-0_TR24-TL0_S0 | 2-BK-2_TS-0_TR24-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
450 | PCU02.INV3-BK-2_TS-0_TR24-TL0_S1 | 2-BK-2_TS-0_TR24-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
451 | PCU02.INV3-BK-2_TS-0_TR25-TL0_S0 | 2-BK-2_TS-0_TR25-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
452 | PCU02.INV3-BK-2_TS-0_TR25-TL0_S1 | 2-BK-2_TS-0_TR25-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
453 | PCU02.INV3-BK-2_TS-0_TR26-TL0_S0 | 2-BK-2_TS-0_TR26-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
454 | PCU02.INV3-BK-2_TS-0_TR26-TL0_S1 | 2-BK-2_TS-0_TR26-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
455 | PCU02.INV3-BK-2_TS-0_TR27-TL0_S0 | 2-BK-2_TS-0_TR27-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
456 | PCU02.INV3-BK-2_TS-0_TR27-TL0_S1 | 2-BK-2_TS-0_TR27-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
457 | PCU02.INV3-BK-2_TS-0_TR28-TL0_S0 | 2-BK-2_TS-0_TR28-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
458 | PCU02.INV3-BK-2_TS-0_TR28-TL0_S1 | 2-BK-2_TS-0_TR28-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
459 | PCU02.INV3-BK-2_TS-0_TR29-TL0_S0 | 2-BK-2_TS-0_TR29-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
460 | PCU02.INV3-BK-2_TS-0_TR29-TL0_S1 | 2-BK-2_TS-0_TR29-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
461 | PCU02.INV4-BK-2_TS-1_TR0-TL0_S0 | 2-BK-2_TS-1_TR0-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
462 | PCU02.INV4-BK-2_TS-1_TR0-TL0_S1 | 2-BK-2_TS-1_TR0-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
463 | PCU02.INV4-BK-2_TS-1_TR1-TL0_S0 | 2-BK-2_TS-1_TR1-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
464 | PCU02.INV4-BK-2_TS-1_TR1-TL0_S1 | 2-BK-2_TS-1_TR1-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
465 | PCU02.INV4-BK-2_TS-1_TR2-TL0_S0 | 2-BK-2_TS-1_TR2-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
466 | PCU02.INV4-BK-2_TS-1_TR2-TL0_S1 | 2-BK-2_TS-1_TR2-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
467 | PCU02.INV4-BK-2_TS-1_TR3-TL0_S0 | 2-BK-2_TS-1_TR3-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
468 | PCU02.INV4-BK-2_TS-1_TR3-TL0_S1 | 2-BK-2_TS-1_TR3-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
469 | PCU02.INV4-BK-2_TS-1_TR4-TL0_S0 | 2-BK-2_TS-1_TR4-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
470 | PCU02.INV4-BK-2_TS-1_TR4-TL0_S1 | 2-BK-2_TS-1_TR4-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
471 | PCU02.INV4-BK-2_TS-1_TR5-TL0_S0 | 2-BK-2_TS-1_TR5-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
472 | PCU02.INV4-BK-2_TS-1_TR5-TL0_S1 | 2-BK-2_TS-1_TR5-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
473 | PCU02.INV4-BK-2_TS-1_TR6-TL0_S0 | 2-BK-2_TS-1_TR6-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
474 | PCU02.INV4-BK-2_TS-1_TR6-TL0_S1 | 2-BK-2_TS-1_TR6-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
475 | PCU02.INV4-BK-2_TS-1_TR7-TL0_S0 | 2-BK-2_TS-1_TR7-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
476 | PCU02.INV4-BK-2_TS-1_TR7-TL0_S1 | 2-BK-2_TS-1_TR7-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
477 | PCU02.INV4-BK-2_TS-1_TR8-TL0_S0 | 2-BK-2_TS-1_TR8-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
478 | PCU02.INV4-BK-2_TS-1_TR8-TL0_S1 | 2-BK-2_TS-1_TR8-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
479 | PCU02.INV4-BK-2_TS-1_TR9-TL0_S0 | 2-BK-2_TS-1_TR9-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
480 | PCU02.INV4-BK-2_TS-1_TR9-TL0_S1 | 2-BK-2_TS-1_TR9-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
481 | PCU02.INV5-BK-2_TS-1_TR10-TL0_S0 | 2-BK-2_TS-1_TR10-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
482 | PCU02.INV5-BK-2_TS-1_TR10-TL0_S1 | 2-BK-2_TS-1_TR10-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
483 | PCU02.INV5-BK-2_TS-1_TR11-TL0_S0 | 2-BK-2_TS-1_TR11-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
484 | PCU02.INV5-BK-2_TS-1_TR11-TL0_S1 | 2-BK-2_TS-1_TR11-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
485 | PCU02.INV5-BK-2_TS-1_TR12-TL0_S0 | 2-BK-2_TS-1_TR12-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
486 | PCU02.INV5-BK-2_TS-1_TR12-TL0_S1 | 2-BK-2_TS-1_TR12-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
487 | PCU02.INV5-BK-2_TS-1_TR13-TL0_S0 | 2-BK-2_TS-1_TR13-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
488 | PCU02.INV5-BK-2_TS-1_TR13-TL0_S1 | 2-BK-2_TS-1_TR13-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
489 | PCU02.INV5-BK-2_TS-1_TR14-TL0_S0 | 2-BK-2_TS-1_TR14-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
490 | PCU02.INV5-BK-2_TS-1_TR14-TL0_S1 | 2-BK-2_TS-1_TR14-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
491 | PCU02.INV5-BK-2_TS-1_TR15-TL0_S0 | 2-BK-2_TS-1_TR15-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
492 | PCU02.INV5-BK-2_TS-1_TR15-TL0_S1 | 2-BK-2_TS-1_TR15-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
493 | PCU02.INV5-BK-2_TS-1_TR16-TL0_S0 | 2-BK-2_TS-1_TR16-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
494 | PCU02.INV5-BK-2_TS-1_TR16-TL0_S1 | 2-BK-2_TS-1_TR16-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
495 | PCU02.INV5-BK-2_TS-1_TR17-TL0_S0 | 2-BK-2_TS-1_TR17-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
496 | PCU02.INV5-BK-2_TS-1_TR17-TL0_S1 | 2-BK-2_TS-1_TR17-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
497 | PCU02.INV5-BK-2_TS-1_TR18-TL0_S0 | 2-BK-2_TS-1_TR18-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
498 | PCU02.INV5-BK-2_TS-1_TR18-TL0_S1 | 2-BK-2_TS-1_TR18-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
499 | PCU02.INV5-BK-2_TS-1_TR19-TL0_S0 | 2-BK-2_TS-1_TR19-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
500 | PCU02.INV5-BK-2_TS-1_TR19-TL0_S1 | 2-BK-2_TS-1_TR19-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
501 | PCU02.INV6-BK-2_TS-1_TR20-TL0_S0 | 2-BK-2_TS-1_TR20-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 159.06 | 79.53 | 79.53 | 37.5 | 1061.2 | 17.31 | 0 | 11.9 | 11.9 | 1.12 | 206.02 | 1.12
502 | PCU02.INV6-BK-2_TS-1_TR20-TL0_S1 | 2-BK-2_TS-1_TR20-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 84.23 | 42.12 | 42.12 | 37.5 | 1061.2 | 17.31 | 0 | 6.3 | 6.3 | 0.59 | 109.1 | 0.59
503 | PCU02.INV6-BK-2_TS-1_TR21-TL0_S0 | 2-BK-2_TS-1_TR21-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
504 | PCU02.INV6-BK-2_TS-1_TR21-TL0_S1 | 2-BK-2_TS-1_TR21-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
505 | PCU02.INV6-BK-2_TS-1_TR22-TL0_S0 | 2-BK-2_TS-1_TR22-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
506 | PCU02.INV6-BK-2_TS-1_TR22-TL0_S1 | 2-BK-2_TS-1_TR22-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
507 | PCU02.INV6-BK-2_TS-1_TR23-TL0_S0 | 2-BK-2_TS-1_TR23-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
508 | PCU02.INV6-BK-2_TS-1_TR23-TL0_S1 | 2-BK-2_TS-1_TR23-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
509 | PCU02.INV6-BK-2_TS-1_TR24-TL0_S0 | 2-BK-2_TS-1_TR24-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
510 | PCU02.INV6-BK-2_TS-1_TR24-TL0_S1 | 2-BK-2_TS-1_TR24-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
511 | PCU02.INV6-BK-2_TS-1_TR25-TL0_S0 | 2-BK-2_TS-1_TR25-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
512 | PCU02.INV6-BK-2_TS-1_TR25-TL0_S1 | 2-BK-2_TS-1_TR25-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
513 | PCU02.INV6-BK-2_TS-1_TR26-TL0_S0 | 2-BK-2_TS-1_TR26-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
514 | PCU02.INV6-BK-2_TS-1_TR26-TL0_S1 | 2-BK-2_TS-1_TR26-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
515 | PCU02.INV6-BK-2_TS-1_TR27-TL0_S0 | 2-BK-2_TS-1_TR27-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
516 | PCU02.INV6-BK-2_TS-1_TR27-TL0_S1 | 2-BK-2_TS-1_TR27-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
517 | PCU02.INV6-BK-2_TS-1_TR28-TL0_S0 | 2-BK-2_TS-1_TR28-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
518 | PCU02.INV6-BK-2_TS-1_TR28-TL0_S1 | 2-BK-2_TS-1_TR28-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
519 | PCU02.INV6-BK-2_TS-1_TR29-TL0_S0 | 2-BK-2_TS-1_TR29-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
520 | PCU02.INV6-BK-2_TS-1_TR29-TL0_S1 | 2-BK-2_TS-1_TR29-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
521 | PCU02.INV7-BK-2_TS-2_TR0-TL0_S0 | 2-BK-2_TS-2_TR0-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
522 | PCU02.INV7-BK-2_TS-2_TR0-TL0_S1 | 2-BK-2_TS-2_TR0-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
523 | PCU02.INV7-BK-2_TS-2_TR1-TL0_S0 | 2-BK-2_TS-2_TR1-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
524 | PCU02.INV7-BK-2_TS-2_TR1-TL0_S1 | 2-BK-2_TS-2_TR1-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
525 | PCU02.INV7-BK-2_TS-2_TR2-TL0_S0 | 2-BK-2_TS-2_TR2-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
526 | PCU02.INV7-BK-2_TS-2_TR2-TL0_S1 | 2-BK-2_TS-2_TR2-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
527 | PCU02.INV7-BK-2_TS-2_TR3-TL0_S0 | 2-BK-2_TS-2_TR3-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
528 | PCU02.INV7-BK-2_TS-2_TR3-TL0_S1 | 2-BK-2_TS-2_TR3-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
529 | PCU02.INV7-BK-2_TS-2_TR4-TL0_S0 | 2-BK-2_TS-2_TR4-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
530 | PCU02.INV7-BK-2_TS-2_TR4-TL0_S1 | 2-BK-2_TS-2_TR4-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
531 | PCU02.INV7-BK-2_TS-2_TR5-TL0_S0 | 2-BK-2_TS-2_TR5-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
532 | PCU02.INV7-BK-2_TS-2_TR5-TL0_S1 | 2-BK-2_TS-2_TR5-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
533 | PCU02.INV7-BK-2_TS-2_TR6-TL0_S0 | 2-BK-2_TS-2_TR6-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
534 | PCU02.INV7-BK-2_TS-2_TR6-TL0_S1 | 2-BK-2_TS-2_TR6-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
535 | PCU02.INV7-BK-2_TS-2_TR7-TL0_S0 | 2-BK-2_TS-2_TR7-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
536 | PCU02.INV7-BK-2_TS-2_TR7-TL0_S1 | 2-BK-2_TS-2_TR7-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
537 | PCU02.INV7-BK-2_TS-2_TR8-TL0_S0 | 2-BK-2_TS-2_TR8-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
538 | PCU02.INV7-BK-2_TS-2_TR8-TL0_S1 | 2-BK-2_TS-2_TR8-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
539 | PCU02.INV7-BK-2_TS-2_TR9-TL0_S0 | 2-BK-2_TS-2_TR9-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
540 | PCU02.INV7-BK-2_TS-2_TR9-TL0_S1 | 2-BK-2_TS-2_TR9-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
541 | PCU02.INV8-BK-2_TS-2_TR10-TL0_S0 | 2-BK-2_TS-2_TR10-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
542 | PCU02.INV8-BK-2_TS-2_TR10-TL0_S1 | 2-BK-2_TS-2_TR10-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
543 | PCU02.INV8-BK-2_TS-2_TR11-TL0_S0 | 2-BK-2_TS-2_TR11-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
544 | PCU02.INV8-BK-2_TS-2_TR11-TL0_S1 | 2-BK-2_TS-2_TR11-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
545 | PCU02.INV8-BK-2_TS-2_TR12-TL0_S0 | 2-BK-2_TS-2_TR12-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
546 | PCU02.INV8-BK-2_TS-2_TR12-TL0_S1 | 2-BK-2_TS-2_TR12-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
547 | PCU02.INV8-BK-2_TS-2_TR13-TL0_S0 | 2-BK-2_TS-2_TR13-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
548 | PCU02.INV8-BK-2_TS-2_TR13-TL0_S1 | 2-BK-2_TS-2_TR13-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
549 | PCU02.INV8-BK-2_TS-2_TR14-TL0_S0 | 2-BK-2_TS-2_TR14-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
550 | PCU02.INV8-BK-2_TS-2_TR14-TL0_S1 | 2-BK-2_TS-2_TR14-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
551 | PCU02.INV8-BK-2_TS-2_TR15-TL0_S0 | 2-BK-2_TS-2_TR15-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
552 | PCU02.INV8-BK-2_TS-2_TR15-TL0_S1 | 2-BK-2_TS-2_TR15-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
553 | PCU02.INV8-BK-2_TS-2_TR16-TL0_S0 | 2-BK-2_TS-2_TR16-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
554 | PCU02.INV8-BK-2_TS-2_TR16-TL0_S1 | 2-BK-2_TS-2_TR16-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
555 | PCU02.INV8-BK-2_TS-2_TR17-TL0_S0 | 2-BK-2_TS-2_TR17-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
556 | PCU02.INV8-BK-2_TS-2_TR17-TL0_S1 | 2-BK-2_TS-2_TR17-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
557 | PCU02.INV8-BK-2_TS-2_TR18-TL0_S0 | 2-BK-2_TS-2_TR18-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
558 | PCU02.INV8-BK-2_TS-2_TR18-TL0_S1 | 2-BK-2_TS-2_TR18-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
559 | PCU02.INV8-BK-2_TS-2_TR19-TL0_S0 | 2-BK-2_TS-2_TR19-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
560 | PCU02.INV8-BK-2_TS-2_TR19-TL0_S1 | 2-BK-2_TS-2_TR19-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
561 | PCU02.INV9-BK-2_TS-2_TR20-TL0_S0 | 2-BK-2_TS-2_TR20-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 159.06 | 79.53 | 79.53 | 37.5 | 1061.2 | 17.31 | 0 | 11.9 | 11.9 | 1.12 | 206.02 | 1.12
562 | PCU02.INV9-BK-2_TS-2_TR20-TL0_S1 | 2-BK-2_TS-2_TR20-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 84.23 | 42.12 | 42.12 | 37.5 | 1061.2 | 17.31 | 0 | 6.3 | 6.3 | 0.59 | 109.1 | 0.59
563 | PCU02.INV9-BK-2_TS-2_TR21-TL0_S0 | 2-BK-2_TS-2_TR21-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
564 | PCU02.INV9-BK-2_TS-2_TR21-TL0_S1 | 2-BK-2_TS-2_TR21-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
565 | PCU02.INV9-BK-2_TS-2_TR22-TL0_S0 | 2-BK-2_TS-2_TR22-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
566 | PCU02.INV9-BK-2_TS-2_TR22-TL0_S1 | 2-BK-2_TS-2_TR22-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
567 | PCU02.INV9-BK-2_TS-2_TR23-TL0_S0 | 2-BK-2_TS-2_TR23-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
568 | PCU02.INV9-BK-2_TS-2_TR23-TL0_S1 | 2-BK-2_TS-2_TR23-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
569 | PCU02.INV9-BK-2_TS-2_TR24-TL0_S0 | 2-BK-2_TS-2_TR24-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
570 | PCU02.INV9-BK-2_TS-2_TR24-TL0_S1 | 2-BK-2_TS-2_TR24-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
571 | PCU02.INV9-BK-2_TS-2_TR25-TL0_S0 | 2-BK-2_TS-2_TR25-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
572 | PCU02.INV9-BK-2_TS-2_TR25-TL0_S1 | 2-BK-2_TS-2_TR25-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
573 | PCU02.INV9-BK-2_TS-2_TR26-TL0_S0 | 2-BK-2_TS-2_TR26-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
574 | PCU02.INV9-BK-2_TS-2_TR26-TL0_S1 | 2-BK-2_TS-2_TR26-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
575 | PCU02.INV9-BK-2_TS-2_TR27-TL0_S0 | 2-BK-2_TS-2_TR27-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
576 | PCU02.INV9-BK-2_TS-2_TR27-TL0_S1 | 2-BK-2_TS-2_TR27-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
577 | PCU02.INV9-BK-2_TS-2_TR28-TL0_S0 | 2-BK-2_TS-2_TR28-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
578 | PCU02.INV9-BK-2_TS-2_TR28-TL0_S1 | 2-BK-2_TS-2_TR28-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
579 | PCU02.INV9-BK-2_TS-2_TR29-TL0_S0 | 2-BK-2_TS-2_TR29-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
580 | PCU02.INV9-BK-2_TS-2_TR29-TL0_S1 | 2-BK-2_TS-2_TR29-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
581 | PCU02.INV10-BK-2_TS-3_TR0-TL0_S0 | 2-BK-2_TS-3_TR0-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
582 | PCU02.INV10-BK-2_TS-3_TR0-TL0_S1 | 2-BK-2_TS-3_TR0-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
583 | PCU02.INV10-BK-2_TS-3_TR1-TL0_S0 | 2-BK-2_TS-3_TR1-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
584 | PCU02.INV10-BK-2_TS-3_TR1-TL0_S1 | 2-BK-2_TS-3_TR1-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
585 | PCU02.INV10-BK-2_TS-3_TR2-TL0_S0 | 2-BK-2_TS-3_TR2-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
586 | PCU02.INV10-BK-2_TS-3_TR2-TL0_S1 | 2-BK-2_TS-3_TR2-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
587 | PCU02.INV10-BK-2_TS-3_TR3-TL0_S0 | 2-BK-2_TS-3_TR3-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
588 | PCU02.INV10-BK-2_TS-3_TR3-TL0_S1 | 2-BK-2_TS-3_TR3-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
589 | PCU02.INV10-BK-2_TS-3_TR4-TL0_S0 | 2-BK-2_TS-3_TR4-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
590 | PCU02.INV10-BK-2_TS-3_TR4-TL0_S1 | 2-BK-2_TS-3_TR4-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
591 | PCU02.INV10-BK-2_TS-3_TR5-TL0_S0 | 2-BK-2_TS-3_TR5-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
592 | PCU02.INV10-BK-2_TS-3_TR5-TL0_S1 | 2-BK-2_TS-3_TR5-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
593 | PCU02.INV10-BK-2_TS-3_TR6-TL0_S0 | 2-BK-2_TS-3_TR6-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
594 | PCU02.INV10-BK-2_TS-3_TR6-TL0_S1 | 2-BK-2_TS-3_TR6-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
595 | PCU02.INV11-BK-2_TN-0_TR0-TL0_S0 | 2-BK-2_TN-0_TR0-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
596 | PCU02.INV11-BK-2_TN-0_TR0-TL0_S1 | 2-BK-2_TN-0_TR0-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
597 | PCU02.INV11-BK-2_TN-0_TR1-TL0_S0 | 2-BK-2_TN-0_TR1-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
598 | PCU02.INV11-BK-2_TN-0_TR1-TL0_S1 | 2-BK-2_TN-0_TR1-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
599 | PCU02.INV11-BK-2_TN-0_TR2-TL0_S0 | 2-BK-2_TN-0_TR2-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
600 | PCU02.INV11-BK-2_TN-0_TR2-TL0_S1 | 2-BK-2_TN-0_TR2-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
601 | PCU02.INV11-BK-2_TN-0_TR3-TL0_S0 | 2-BK-2_TN-0_TR3-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
602 | PCU02.INV11-BK-2_TN-0_TR3-TL0_S1 | 2-BK-2_TN-0_TR3-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
603 | PCU02.INV11-BK-2_TN-0_TR4-TL0_S0 | 2-BK-2_TN-0_TR4-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
604 | PCU02.INV11-BK-2_TN-0_TR4-TL0_S1 | 2-BK-2_TN-0_TR4-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
605 | PCU02.INV11-BK-2_TN-0_TR5-TL0_S0 | 2-BK-2_TN-0_TR5-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
606 | PCU02.INV11-BK-2_TN-0_TR5-TL0_S1 | 2-BK-2_TN-0_TR5-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
607 | PCU02.INV11-BK-2_TN-0_TR6-TL0_S0 | 2-BK-2_TN-0_TR6-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
608 | PCU02.INV11-BK-2_TN-0_TR6-TL0_S1 | 2-BK-2_TN-0_TR6-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
609 | PCU02.INV11-BK-2_TN-0_TR7-TL0_S0 | 2-BK-2_TN-0_TR7-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
610 | PCU02.INV11-BK-2_TN-0_TR7-TL0_S1 | 2-BK-2_TN-0_TR7-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
611 | PCU02.INV11-BK-2_TN-0_TR8-TL0_S0 | 2-BK-2_TN-0_TR8-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
612 | PCU02.INV11-BK-2_TN-0_TR8-TL0_S1 | 2-BK-2_TN-0_TR8-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
613 | PCU02.INV11-BK-2_TN-0_TR9-TL0_S0 | 2-BK-2_TN-0_TR9-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
614 | PCU02.INV11-BK-2_TN-0_TR9-TL0_S1 | 2-BK-2_TN-0_TR9-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
615 | PCU02.INV12-BK-2_TN-0_TR10-TL0_S0 | 2-BK-2_TN-0_TR10-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
616 | PCU02.INV12-BK-2_TN-0_TR10-TL0_S1 | 2-BK-2_TN-0_TR10-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
617 | PCU02.INV12-BK-2_TN-0_TR11-TL0_S0 | 2-BK-2_TN-0_TR11-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
618 | PCU02.INV12-BK-2_TN-0_TR11-TL0_S1 | 2-BK-2_TN-0_TR11-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
619 | PCU02.INV12-BK-2_TN-0_TR12-TL0_S0 | 2-BK-2_TN-0_TR12-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
620 | PCU02.INV12-BK-2_TN-0_TR12-TL0_S1 | 2-BK-2_TN-0_TR12-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
621 | PCU02.INV12-BK-2_TN-0_TR13-TL0_S0 | 2-BK-2_TN-0_TR13-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
622 | PCU02.INV12-BK-2_TN-0_TR13-TL0_S1 | 2-BK-2_TN-0_TR13-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
623 | PCU02.INV12-BK-2_TN-0_TR14-TL0_S0 | 2-BK-2_TN-0_TR14-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
624 | PCU02.INV12-BK-2_TN-0_TR14-TL0_S1 | 2-BK-2_TN-0_TR14-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
625 | PCU02.INV12-BK-2_TN-0_TR15-TL0_S0 | 2-BK-2_TN-0_TR15-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
626 | PCU02.INV12-BK-2_TN-0_TR15-TL0_S1 | 2-BK-2_TN-0_TR15-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
627 | PCU02.INV12-BK-2_TN-0_TR16-TL0_S0 | 2-BK-2_TN-0_TR16-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
628 | PCU02.INV12-BK-2_TN-0_TR16-TL0_S1 | 2-BK-2_TN-0_TR16-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
629 | PCU02.INV12-BK-2_TN-0_TR17-TL0_S0 | 2-BK-2_TN-0_TR17-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
630 | PCU02.INV12-BK-2_TN-0_TR17-TL0_S1 | 2-BK-2_TN-0_TR17-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
631 | PCU02.INV12-BK-2_TN-0_TR18-TL0_S0 | 2-BK-2_TN-0_TR18-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
632 | PCU02.INV12-BK-2_TN-0_TR18-TL0_S1 | 2-BK-2_TN-0_TR18-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
633 | PCU02.INV12-BK-2_TN-0_TR19-TL0_S0 | 2-BK-2_TN-0_TR19-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
634 | PCU02.INV12-BK-2_TN-0_TR19-TL0_S1 | 2-BK-2_TN-0_TR19-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
635 | PCU02.INV13-BK-2_TN-0_TR20-TL0_S0 | 2-BK-2_TN-0_TR20-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 84.23 | 42.12 | 42.12 | 37.5 | 1061.2 | 17.31 | 0 | 6.3 | 6.3 | 0.59 | 109.1 | 0.59
636 | PCU02.INV13-BK-2_TN-0_TR20-TL0_S1 | 2-BK-2_TN-0_TR20-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 159.06 | 79.53 | 79.53 | 37.5 | 1061.2 | 17.31 | 0 | 11.9 | 11.9 | 1.12 | 206.02 | 1.12
637 | PCU02.INV13-BK-2_TN-0_TR21-TL0_S0 | 2-BK-2_TN-0_TR21-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
638 | PCU02.INV13-BK-2_TN-0_TR21-TL0_S1 | 2-BK-2_TN-0_TR21-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
639 | PCU02.INV13-BK-2_TN-0_TR22-TL0_S0 | 2-BK-2_TN-0_TR22-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
640 | PCU02.INV13-BK-2_TN-0_TR22-TL0_S1 | 2-BK-2_TN-0_TR22-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
641 | PCU02.INV13-BK-2_TN-0_TR23-TL0_S0 | 2-BK-2_TN-0_TR23-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
642 | PCU02.INV13-BK-2_TN-0_TR23-TL0_S1 | 2-BK-2_TN-0_TR23-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
643 | PCU02.INV13-BK-2_TN-0_TR24-TL0_S0 | 2-BK-2_TN-0_TR24-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
644 | PCU02.INV13-BK-2_TN-0_TR24-TL0_S1 | 2-BK-2_TN-0_TR24-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
645 | PCU02.INV13-BK-2_TN-0_TR25-TL0_S0 | 2-BK-2_TN-0_TR25-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
646 | PCU02.INV13-BK-2_TN-0_TR25-TL0_S1 | 2-BK-2_TN-0_TR25-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
647 | PCU02.INV13-BK-2_TN-0_TR26-TL0_S0 | 2-BK-2_TN-0_TR26-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
648 | PCU02.INV13-BK-2_TN-0_TR26-TL0_S1 | 2-BK-2_TN-0_TR26-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
649 | PCU02.INV13-BK-2_TN-0_TR27-TL0_S0 | 2-BK-2_TN-0_TR27-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
650 | PCU02.INV13-BK-2_TN-0_TR27-TL0_S1 | 2-BK-2_TN-0_TR27-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
651 | PCU02.INV13-BK-2_TN-0_TR28-TL0_S0 | 2-BK-2_TN-0_TR28-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
652 | PCU02.INV13-BK-2_TN-0_TR28-TL0_S1 | 2-BK-2_TN-0_TR28-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
653 | PCU02.INV13-BK-2_TN-0_TR29-TL0_S0 | 2-BK-2_TN-0_TR29-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
654 | PCU02.INV13-BK-2_TN-0_TR29-TL0_S1 | 2-BK-2_TN-0_TR29-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
655 | PCU02.INV14-BK-2_TN-1_TR0-TL0_S0 | 2-BK-2_TN-1_TR0-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
656 | PCU02.INV14-BK-2_TN-1_TR0-TL0_S1 | 2-BK-2_TN-1_TR0-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
657 | PCU02.INV14-BK-2_TN-1_TR1-TL0_S0 | 2-BK-2_TN-1_TR1-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
658 | PCU02.INV14-BK-2_TN-1_TR1-TL0_S1 | 2-BK-2_TN-1_TR1-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
659 | PCU02.INV14-BK-2_TN-1_TR2-TL0_S0 | 2-BK-2_TN-1_TR2-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
660 | PCU02.INV14-BK-2_TN-1_TR2-TL0_S1 | 2-BK-2_TN-1_TR2-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
661 | PCU02.INV14-BK-2_TN-1_TR3-TL0_S0 | 2-BK-2_TN-1_TR3-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
662 | PCU02.INV14-BK-2_TN-1_TR3-TL0_S1 | 2-BK-2_TN-1_TR3-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
663 | PCU02.INV14-BK-2_TN-1_TR4-TL0_S0 | 2-BK-2_TN-1_TR4-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
664 | PCU02.INV14-BK-2_TN-1_TR4-TL0_S1 | 2-BK-2_TN-1_TR4-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
665 | PCU02.INV14-BK-2_TN-1_TR5-TL0_S0 | 2-BK-2_TN-1_TR5-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
666 | PCU02.INV14-BK-2_TN-1_TR5-TL0_S1 | 2-BK-2_TN-1_TR5-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
667 | PCU02.INV14-BK-2_TN-1_TR6-TL0_S0 | 2-BK-2_TN-1_TR6-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
668 | PCU02.INV14-BK-2_TN-1_TR6-TL0_S1 | 2-BK-2_TN-1_TR6-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
669 | PCU02.INV14-BK-2_TN-1_TR7-TL0_S0 | 2-BK-2_TN-1_TR7-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
670 | PCU02.INV14-BK-2_TN-1_TR7-TL0_S1 | 2-BK-2_TN-1_TR7-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
671 | PCU02.INV14-BK-2_TN-1_TR8-TL0_S0 | 2-BK-2_TN-1_TR8-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
672 | PCU02.INV14-BK-2_TN-1_TR8-TL0_S1 | 2-BK-2_TN-1_TR8-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
673 | PCU02.INV14-BK-2_TN-1_TR9-TL0_S0 | 2-BK-2_TN-1_TR9-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
674 | PCU02.INV14-BK-2_TN-1_TR9-TL0_S1 | 2-BK-2_TN-1_TR9-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
675 | PCU02.INV14-BK-2_TN-1_TR10-TL0_S0 | 2-BK-2_TN-1_TR10-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
676 | PCU02.INV14-BK-2_TN-1_TR10-TL0_S1 | 2-BK-2_TN-1_TR10-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
677 | PCU02.INV15-BK-2_TN-1_TR19-TL0_S1 | 2-BK-2_TN-1_TR19-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 169.16 | 84.58 | 84.58 | 42.5 | 1061.2 | 17.31 | 0 | 12.66 | 12.66 | 1.19 | 219.1 | 1.19
678 | PCU02.INV15-BK-2_TN-1_TR20-TL0_S0 | 2-BK-2_TN-1_TR20-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 84.23 | 42.12 | 42.12 | 37.5 | 1061.2 | 17.31 | 0 | 6.3 | 6.3 | 0.59 | 109.1 | 0.59
679 | PCU02.INV15-BK-2_TN-1_TR20-TL0_S1 | 2-BK-2_TN-1_TR20-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 159.06 | 79.53 | 79.53 | 37.5 | 1061.2 | 17.31 | 0 | 11.9 | 11.9 | 1.12 | 206.02 | 1.12
680 | PCU02.INV15-BK-2_TN-1_TR21-TL0_S0 | 2-BK-2_TN-1_TR21-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
681 | PCU02.INV15-BK-2_TN-1_TR21-TL0_S1 | 2-BK-2_TN-1_TR21-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
682 | PCU02.INV15-BK-2_TN-1_TR22-TL0_S0 | 2-BK-2_TN-1_TR22-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
683 | PCU02.INV15-BK-2_TN-1_TR22-TL0_S1 | 2-BK-2_TN-1_TR22-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
684 | PCU02.INV15-BK-2_TN-1_TR23-TL0_S0 | 2-BK-2_TN-1_TR23-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
685 | PCU02.INV15-BK-2_TN-1_TR23-TL0_S1 | 2-BK-2_TN-1_TR23-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
686 | PCU02.INV15-BK-2_TN-1_TR24-TL0_S0 | 2-BK-2_TN-1_TR24-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
687 | PCU02.INV15-BK-2_TN-1_TR24-TL0_S1 | 2-BK-2_TN-1_TR24-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
688 | PCU02.INV15-BK-2_TN-1_TR25-TL0_S0 | 2-BK-2_TN-1_TR25-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
689 | PCU02.INV15-BK-2_TN-1_TR25-TL0_S1 | 2-BK-2_TN-1_TR25-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
690 | PCU02.INV15-BK-2_TN-1_TR26-TL0_S0 | 2-BK-2_TN-1_TR26-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
691 | PCU02.INV15-BK-2_TN-1_TR26-TL0_S1 | 2-BK-2_TN-1_TR26-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
692 | PCU02.INV15-BK-2_TN-1_TR27-TL0_S0 | 2-BK-2_TN-1_TR27-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
693 | PCU02.INV15-BK-2_TN-1_TR27-TL0_S1 | 2-BK-2_TN-1_TR27-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
694 | PCU02.INV15-BK-2_TN-1_TR28-TL0_S0 | 2-BK-2_TN-1_TR28-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
695 | PCU02.INV15-BK-2_TN-1_TR28-TL0_S1 | 2-BK-2_TN-1_TR28-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
696 | PCU02.INV15-BK-2_TN-1_TR29-TL0_S0 | 2-BK-2_TN-1_TR29-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
697 | PCU02.INV15-BK-2_TN-1_TR29-TL0_S1 | 2-BK-2_TN-1_TR29-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
698 | PCU02.INV16-BK-2_TN-2_TR0-TL0_S0 | 2-BK-2_TN-2_TR0-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
699 | PCU02.INV16-BK-2_TN-2_TR0-TL0_S1 | 2-BK-2_TN-2_TR0-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
700 | PCU02.INV16-BK-2_TN-2_TR1-TL0_S0 | 2-BK-2_TN-2_TR1-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
701 | PCU02.INV16-BK-2_TN-2_TR1-TL0_S1 | 2-BK-2_TN-2_TR1-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
702 | PCU02.INV16-BK-2_TN-2_TR2-TL0_S0 | 2-BK-2_TN-2_TR2-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
703 | PCU02.INV16-BK-2_TN-2_TR2-TL0_S1 | 2-BK-2_TN-2_TR2-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
704 | PCU02.INV16-BK-2_TN-2_TR3-TL0_S0 | 2-BK-2_TN-2_TR3-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
705 | PCU02.INV16-BK-2_TN-2_TR3-TL0_S1 | 2-BK-2_TN-2_TR3-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
706 | PCU02.INV16-BK-2_TN-2_TR4-TL0_S0 | 2-BK-2_TN-2_TR4-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
707 | PCU02.INV16-BK-2_TN-2_TR4-TL0_S1 | 2-BK-2_TN-2_TR4-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
708 | PCU02.INV16-BK-2_TN-2_TR5-TL0_S0 | 2-BK-2_TN-2_TR5-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
709 | PCU02.INV16-BK-2_TN-2_TR5-TL0_S1 | 2-BK-2_TN-2_TR5-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
710 | PCU02.INV16-BK-2_TN-2_TR6-TL0_S0 | 2-BK-2_TN-2_TR6-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
711 | PCU02.INV16-BK-2_TN-2_TR6-TL0_S1 | 2-BK-2_TN-2_TR6-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
712 | PCU02.INV16-BK-2_TN-2_TR7-TL0_S0 | 2-BK-2_TN-2_TR7-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
713 | PCU02.INV16-BK-2_TN-2_TR7-TL0_S1 | 2-BK-2_TN-2_TR7-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
714 | PCU02.INV16-BK-2_TN-2_TR8-TL0_S0 | 2-BK-2_TN-2_TR8-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
715 | PCU02.INV16-BK-2_TN-2_TR8-TL0_S1 | 2-BK-2_TN-2_TR8-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
716 | PCU02.INV16-BK-2_TN-2_TR9-TL0_S0 | 2-BK-2_TN-2_TR9-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
717 | PCU02.INV16-BK-2_TN-2_TR9-TL0_S1 | 2-BK-2_TN-2_TR9-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
718 | PCU02.INV16-BK-2_TN-2_TR10-TL0_S0 | 2-BK-2_TN-2_TR10-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
719 | PCU02.INV17-BK-2_TN-2_TR19-TL0_S1 | 2-BK-2_TN-2_TR19-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 169.16 | 84.58 | 84.58 | 42.5 | 1061.2 | 17.31 | 0 | 12.66 | 12.66 | 1.19 | 219.1 | 1.19
720 | PCU02.INV17-BK-2_TN-2_TR20-TL0_S0 | 2-BK-2_TN-2_TR20-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 84.23 | 42.12 | 42.12 | 37.5 | 1061.2 | 17.31 | 0 | 6.3 | 6.3 | 0.59 | 109.1 | 0.59
721 | PCU02.INV17-BK-2_TN-2_TR20-TL0_S1 | 2-BK-2_TN-2_TR20-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 159.06 | 79.53 | 79.53 | 37.5 | 1061.2 | 17.31 | 0 | 11.9 | 11.9 | 1.12 | 206.02 | 1.12
722 | PCU02.INV17-BK-2_TN-2_TR21-TL0_S0 | 2-BK-2_TN-2_TR21-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
723 | PCU02.INV17-BK-2_TN-2_TR21-TL0_S1 | 2-BK-2_TN-2_TR21-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
724 | PCU02.INV17-BK-2_TN-2_TR22-TL0_S0 | 2-BK-2_TN-2_TR22-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
725 | PCU02.INV17-BK-2_TN-2_TR22-TL0_S1 | 2-BK-2_TN-2_TR22-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
726 | PCU02.INV17-BK-2_TN-2_TR23-TL0_S0 | 2-BK-2_TN-2_TR23-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
727 | PCU02.INV17-BK-2_TN-2_TR23-TL0_S1 | 2-BK-2_TN-2_TR23-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
728 | PCU02.INV17-BK-2_TN-2_TR24-TL0_S0 | 2-BK-2_TN-2_TR24-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
729 | PCU02.INV17-BK-2_TN-2_TR24-TL0_S1 | 2-BK-2_TN-2_TR24-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
730 | PCU02.INV17-BK-2_TN-2_TR25-TL0_S0 | 2-BK-2_TN-2_TR25-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
731 | PCU02.INV17-BK-2_TN-2_TR25-TL0_S1 | 2-BK-2_TN-2_TR25-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
732 | PCU02.INV17-BK-2_TN-2_TR26-TL0_S0 | 2-BK-2_TN-2_TR26-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
733 | PCU02.INV17-BK-2_TN-2_TR26-TL0_S1 | 2-BK-2_TN-2_TR26-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
734 | PCU02.INV17-BK-2_TN-2_TR27-TL0_S0 | 2-BK-2_TN-2_TR27-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
735 | PCU02.INV17-BK-2_TN-2_TR27-TL0_S1 | 2-BK-2_TN-2_TR27-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
736 | PCU02.INV17-BK-2_TN-2_TR28-TL0_S0 | 2-BK-2_TN-2_TR28-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
737 | PCU02.INV17-BK-2_TN-2_TR28-TL0_S1 | 2-BK-2_TN-2_TR28-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
738 | PCU02.INV17-BK-2_TN-2_TR29-TL0_S0 | 2-BK-2_TN-2_TR29-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
739 | PCU02.INV17-BK-2_TN-2_TR29-TL0_S1 | 2-BK-2_TN-2_TR29-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
740 | PCU02.INV18-BK-2_TN-3_TR3-TL0_S1 | 2-BK-2_TN-3_TR3-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
741 | PCU02.INV18-BK-2_TN-3_TR4-TL0_S0 | 2-BK-2_TN-3_TR4-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
742 | PCU02.INV18-BK-2_TN-3_TR4-TL0_S1 | 2-BK-2_TN-3_TR4-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
743 | PCU02.INV18-BK-2_TN-3_TR5-TL0_S0 | 2-BK-2_TN-3_TR5-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
744 | PCU02.INV18-BK-2_TN-3_TR5-TL0_S1 | 2-BK-2_TN-3_TR5-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
745 | PCU02.INV18-BK-2_TN-3_TR6-TL0_S0 | 2-BK-2_TN-3_TR6-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
746 | PCU02.INV18-BK-2_TN-3_TR6-TL0_S1 | 2-BK-2_TN-3_TR6-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
747 | PCU02.INV18-BK-2_TN-3_TR7-TL0_S0 | 2-BK-2_TN-3_TR7-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
748 | PCU02.INV18-BK-2_TN-3_TR7-TL0_S1 | 2-BK-2_TN-3_TR7-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
749 | PCU02.INV18-BK-2_TN-3_TR8-TL0_S0 | 2-BK-2_TN-3_TR8-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
750 | PCU02.INV18-BK-2_TN-3_TR8-TL0_S1 | 2-BK-2_TN-3_TR8-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
751 | PCU02.INV18-BK-2_TN-3_TR9-TL0_S0 | 2-BK-2_TN-3_TR9-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
752 | PCU02.INV18-BK-2_TN-3_TR9-TL0_S1 | 2-BK-2_TN-3_TR9-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
753 | PCU02.INV18-BK-2_TN-3_TR10-TL0_S0 | 2-BK-2_TN-3_TR10-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
754 | PCU02.INV18-BK-2_TN-3_TR10-TL0_S1 | 2-BK-2_TN-3_TR10-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
755 | PCU02.INV18-BK-2_TN-3_TR11-TL0_S0 | 2-BK-2_TN-3_TR11-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
756 | PCU02.INV18-BK-2_TN-3_TR11-TL0_S1 | 2-BK-2_TN-3_TR11-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
757 | PCU02.INV18-BK-2_TN-3_TR12-TL0_S0 | 2-BK-2_TN-3_TR12-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
758 | PCU02.INV18-BK-2_TN-3_TR12-TL0_S1 | 2-BK-2_TN-3_TR12-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
759 | PCU02.INV18-BK-2_TN-3_TR13-TL0_S0 | 2-BK-2_TN-3_TR13-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
760 | PCU02.INV18-BK-2_TN-3_TR13-TL0_S1 | 2-BK-2_TN-3_TR13-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
761 | PCU02.INV19-BK-2_TN-1_TR11-TL0_S0 | 2-BK-2_TN-1_TR11-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 205.13 | 102.56 | 102.56 | 26.28 | 1061.2 | 17.31 | 0 | 15.35 | 15.35 | 1.45 | 265.68 | 1.45
762 | PCU02.INV19-BK-2_TN-1_TR11-TL0_S1 | 2-BK-2_TN-1_TR11-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 130.3 | 65.15 | 65.15 | 26.28 | 1061.2 | 17.31 | 0 | 9.75 | 9.75 | 0.92 | 168.76 | 0.92
763 | PCU02.INV19-BK-2_TN-1_TR12-TL0_S0 | 2-BK-2_TN-1_TR12-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 195.03 | 97.51 | 97.51 | 21.28 | 1061.2 | 17.31 | 0 | 14.59 | 14.59 | 1.38 | 252.6 | 1.38
764 | PCU02.INV19-BK-2_TN-1_TR12-TL0_S1 | 2-BK-2_TN-1_TR12-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 120.2 | 60.1 | 60.1 | 21.28 | 1061.2 | 17.31 | 0 | 8.99 | 8.99 | 0.85 | 155.68 | 0.85
765 | PCU02.INV19-BK-2_TN-1_TR13-TL0_S0 | 2-BK-2_TN-1_TR13-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 184.93 | 92.46 | 92.46 | 16.28 | 1061.2 | 17.31 | 0 | 13.84 | 13.84 | 1.3 | 239.52 | 1.31
766 | PCU02.INV19-BK-2_TN-1_TR13-TL0_S1 | 2-BK-2_TN-1_TR13-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 110.1 | 55.05 | 55.05 | 16.28 | 1061.2 | 17.31 | 0 | 8.24 | 8.24 | 0.78 | 142.6 | 0.78
767 | PCU02.INV19-BK-2_TN-1_TR14-TL0_S0 | 2-BK-2_TN-1_TR14-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 174.83 | 87.41 | 87.41 | 11.28 | 1061.2 | 17.31 | 0 | 13.08 | 13.08 | 1.23 | 226.44 | 1.23
768 | PCU02.INV19-BK-2_TN-1_TR14-TL0_S1 | 2-BK-2_TN-1_TR14-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 100 | 50 | 50 | 11.28 | 1061.2 | 17.31 | 0 | 7.48 | 7.48 | 0.71 | 129.52 | 0.71
769 | PCU02.INV19-BK-2_TN-1_TR15-TL0_S0 | 2-BK-2_TN-1_TR15-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 164.73 | 82.36 | 82.36 | 6.28 | 1061.2 | 17.31 | 0 | 12.33 | 12.33 | 1.16 | 213.35 | 1.16
770 | PCU02.INV19-BK-2_TN-1_TR15-TL0_S1 | 2-BK-2_TN-1_TR15-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 89.9 | 44.95 | 44.95 | 6.28 | 1061.2 | 17.31 | 0 | 6.73 | 6.73 | 0.63 | 116.43 | 0.63
771 | PCU02.INV19-BK-2_TN-1_TR16-TL0_S0 | 2-BK-2_TN-1_TR16-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 174.83 | 87.41 | 87.41 | 11.28 | 1061.2 | 17.31 | 0 | 13.08 | 13.08 | 1.23 | 226.44 | 1.23
772 | PCU02.INV19-BK-2_TN-1_TR16-TL0_S1 | 2-BK-2_TN-1_TR16-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 100 | 50 | 50 | 11.28 | 1061.2 | 17.31 | 0 | 7.48 | 7.48 | 0.71 | 129.52 | 0.71
773 | PCU02.INV19-BK-2_TN-1_TR17-TL0_S0 | 2-BK-2_TN-1_TR17-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 184.93 | 92.46 | 92.46 | 16.28 | 1061.2 | 17.31 | 0 | 13.84 | 13.84 | 1.3 | 239.52 | 1.31
774 | PCU02.INV19-BK-2_TN-1_TR17-TL0_S1 | 2-BK-2_TN-1_TR17-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 110.1 | 55.05 | 55.05 | 16.28 | 1061.2 | 17.31 | 0 | 8.24 | 8.24 | 0.78 | 142.6 | 0.78
775 | PCU02.INV19-BK-2_TN-1_TR18-TL0_S0 | 2-BK-2_TN-1_TR18-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 195.03 | 97.51 | 97.51 | 21.28 | 1061.2 | 17.31 | 0 | 14.59 | 14.59 | 1.38 | 252.6 | 1.38
776 | PCU02.INV19-BK-2_TN-1_TR18-TL0_S1 | 2-BK-2_TN-1_TR18-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 120.2 | 60.1 | 60.1 | 21.28 | 1061.2 | 17.31 | 0 | 8.99 | 8.99 | 0.85 | 155.68 | 0.85
777 | PCU02.INV19-BK-2_TN-1_TR19-TL0_S0 | 2-BK-2_TN-1_TR19-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 205.13 | 102.56 | 102.56 | 26.28 | 1061.2 | 17.31 | 0 | 15.35 | 15.35 | 1.45 | 265.68 | 1.45
778 | PCU02.INV19-BK-2_TN-2_TR17-TL0_S1 | 2-BK-2_TN-2_TR17-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
779 | PCU02.INV19-BK-2_TN-2_TR18-TL0_S0 | 2-BK-2_TN-2_TR18-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
780 | PCU02.INV19-BK-2_TN-2_TR18-TL0_S1 | 2-BK-2_TN-2_TR18-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
781 | PCU02.INV19-BK-2_TN-2_TR19-TL0_S0 | 2-BK-2_TN-2_TR19-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
782 | PCU02.INV20-BK-2_TN-2_TR10-TL0_S1 | 2-BK-2_TN-2_TR10-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 150.5 | 75.25 | 75.25 | 36.28 | 1061.2 | 17.31 | 0 | 11.26 | 11.26 | 1.06 | 194.92 | 1.06
783 | PCU02.INV20-BK-2_TN-2_TR11-TL0_S0 | 2-BK-2_TN-2_TR11-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 215.23 | 107.61 | 107.61 | 31.28 | 1061.2 | 17.31 | 0 | 16.1 | 16.1 | 1.52 | 278.76 | 1.52
784 | PCU02.INV20-BK-2_TN-2_TR11-TL0_S1 | 2-BK-2_TN-2_TR11-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 140.4 | 70.2 | 70.2 | 31.28 | 1061.2 | 17.31 | 0 | 10.5 | 10.5 | 0.99 | 181.84 | 0.99
785 | PCU02.INV20-BK-2_TN-2_TR12-TL0_S0 | 2-BK-2_TN-2_TR12-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 205.13 | 102.56 | 102.56 | 26.28 | 1061.2 | 17.31 | 0 | 15.35 | 15.35 | 1.45 | 265.68 | 1.45
786 | PCU02.INV20-BK-2_TN-2_TR12-TL0_S1 | 2-BK-2_TN-2_TR12-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 130.3 | 65.15 | 65.15 | 26.28 | 1061.2 | 17.31 | 0 | 9.75 | 9.75 | 0.92 | 168.76 | 0.92
787 | PCU02.INV20-BK-2_TN-2_TR13-TL0_S0 | 2-BK-2_TN-2_TR13-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 195.03 | 97.51 | 97.51 | 21.28 | 1061.2 | 17.31 | 0 | 14.59 | 14.59 | 1.38 | 252.6 | 1.38
788 | PCU02.INV20-BK-2_TN-2_TR13-TL0_S1 | 2-BK-2_TN-2_TR13-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 120.2 | 60.1 | 60.1 | 21.28 | 1061.2 | 17.31 | 0 | 8.99 | 8.99 | 0.85 | 155.68 | 0.85
789 | PCU02.INV20-BK-2_TN-2_TR14-TL0_S0 | 2-BK-2_TN-2_TR14-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 205.13 | 102.56 | 102.56 | 26.28 | 1061.2 | 17.31 | 0 | 15.35 | 15.35 | 1.45 | 265.68 | 1.45
790 | PCU02.INV20-BK-2_TN-2_TR14-TL0_S1 | 2-BK-2_TN-2_TR14-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 130.3 | 65.15 | 65.15 | 26.28 | 1061.2 | 17.31 | 0 | 9.75 | 9.75 | 0.92 | 168.76 | 0.92
791 | PCU02.INV20-BK-2_TN-2_TR15-TL0_S0 | 2-BK-2_TN-2_TR15-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 215.23 | 107.61 | 107.61 | 31.28 | 1061.2 | 17.31 | 0 | 16.1 | 16.1 | 1.52 | 278.76 | 1.52
792 | PCU02.INV20-BK-2_TN-2_TR15-TL0_S1 | 2-BK-2_TN-2_TR15-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 140.4 | 70.2 | 70.2 | 31.28 | 1061.2 | 17.31 | 0 | 10.5 | 10.5 | 0.99 | 181.84 | 0.99
793 | PCU02.INV20-BK-2_TN-2_TR16-TL0_S0 | 2-BK-2_TN-2_TR16-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 225.33 | 112.66 | 112.66 | 36.28 | 1061.2 | 17.31 | 0 | 16.86 | 16.86 | 1.59 | 291.84 | 1.59
794 | PCU02.INV20-BK-2_TN-2_TR16-TL0_S1 | 2-BK-2_TN-2_TR16-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 150.5 | 75.25 | 75.25 | 36.28 | 1061.2 | 17.31 | 0 | 11.26 | 11.26 | 1.06 | 194.92 | 1.06
795 | PCU02.INV20-BK-2_TN-2_TR17-TL0_S0 | 2-BK-2_TN-2_TR17-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 235.43 | 117.71 | 117.71 | 41.28 | 1061.2 | 17.31 | 0 | 17.62 | 17.62 | 1.66 | 304.93 | 1.66
796 | PCU02.INV20-BK-2_TN-3_TR0-TL0_S0 | 2-BK-2_TN-3_TR0-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
797 | PCU02.INV20-BK-2_TN-3_TR0-TL0_S1 | 2-BK-2_TN-3_TR0-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
798 | PCU02.INV20-BK-2_TN-3_TR1-TL0_S0 | 2-BK-2_TN-3_TR1-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
799 | PCU02.INV20-BK-2_TN-3_TR1-TL0_S1 | 2-BK-2_TN-3_TR1-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
800 | PCU02.INV20-BK-2_TN-3_TR2-TL0_S0 | 2-BK-2_TN-3_TR2-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
801 | PCU02.INV20-BK-2_TN-3_TR2-TL0_S1 | 2-BK-2_TN-3_TR2-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
802 | PCU02.INV20-BK-2_TN-3_TR3-TL0_S0 | 2-BK-2_TN-3_TR3-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 2 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
803 | PCU03.INV1-BK-3_TS-0_TR0-TL0_S0 | 3-BK-3_TS-0_TR0-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
804 | PCU03.INV1-BK-3_TS-0_TR0-TL0_S1 | 3-BK-3_TS-0_TR0-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
805 | PCU03.INV1-BK-3_TS-0_TR1-TL0_S0 | 3-BK-3_TS-0_TR1-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
806 | PCU03.INV1-BK-3_TS-0_TR1-TL0_S1 | 3-BK-3_TS-0_TR1-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
807 | PCU03.INV1-BK-3_TS-0_TR2-TL0_S0 | 3-BK-3_TS-0_TR2-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
808 | PCU03.INV1-BK-3_TS-0_TR2-TL0_S1 | 3-BK-3_TS-0_TR2-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
809 | PCU03.INV1-BK-3_TS-0_TR3-TL0_S0 | 3-BK-3_TS-0_TR3-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
810 | PCU03.INV1-BK-3_TS-0_TR3-TL0_S1 | 3-BK-3_TS-0_TR3-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
811 | PCU03.INV1-BK-3_TS-0_TR4-TL0_S0 | 3-BK-3_TS-0_TR4-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
812 | PCU03.INV1-BK-3_TS-0_TR4-TL0_S1 | 3-BK-3_TS-0_TR4-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
813 | PCU03.INV1-BK-3_TS-0_TR5-TL0_S0 | 3-BK-3_TS-0_TR5-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
814 | PCU03.INV1-BK-3_TS-0_TR5-TL0_S1 | 3-BK-3_TS-0_TR5-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
815 | PCU03.INV1-BK-3_TS-0_TR6-TL0_S0 | 3-BK-3_TS-0_TR6-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
816 | PCU03.INV1-BK-3_TS-0_TR6-TL0_S1 | 3-BK-3_TS-0_TR6-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
817 | PCU03.INV1-BK-3_TS-0_TR7-TL0_S1 | 3-BK-3_TS-0_TR7-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
818 | PCU03.INV2-BK-3_TS-0_TR7-TL0_S0 | 3-BK-3_TS-0_TR7-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
819 | PCU03.INV2-BK-3_TS-0_TR8-TL0_S0 | 3-BK-3_TS-0_TR8-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
820 | PCU03.INV2-BK-3_TS-0_TR8-TL0_S1 | 3-BK-3_TS-0_TR8-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
821 | PCU03.INV2-BK-3_TS-0_TR9-TL0_S0 | 3-BK-3_TS-0_TR9-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
822 | PCU03.INV2-BK-3_TS-0_TR9-TL0_S1 | 3-BK-3_TS-0_TR9-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
823 | PCU03.INV2-BK-3_TS-0_TR10-TL0_S0 | 3-BK-3_TS-0_TR10-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
824 | PCU03.INV2-BK-3_TS-0_TR10-TL0_S1 | 3-BK-3_TS-0_TR10-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
825 | PCU03.INV2-BK-3_TS-0_TR11-TL0_S0 | 3-BK-3_TS-0_TR11-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
826 | PCU03.INV2-BK-3_TS-0_TR11-TL0_S1 | 3-BK-3_TS-0_TR11-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
827 | PCU03.INV2-BK-3_TS-0_TR12-TL0_S0 | 3-BK-3_TS-0_TR12-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
828 | PCU03.INV2-BK-3_TS-0_TR12-TL0_S1 | 3-BK-3_TS-0_TR12-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
829 | PCU03.INV2-BK-3_TS-0_TR13-TL0_S0 | 3-BK-3_TS-0_TR13-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
830 | PCU03.INV2-BK-3_TS-0_TR13-TL0_S1 | 3-BK-3_TS-0_TR13-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
831 | PCU03.INV2-BK-3_TS-0_TR14-TL0_S0 | 3-BK-3_TS-0_TR14-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
832 | PCU03.INV2-BK-3_TS-0_TR14-TL0_S1 | 3-BK-3_TS-0_TR14-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
833 | PCU03.INV3-BK-3_TS-0_TR15-TL0_S0 | 3-BK-3_TS-0_TR15-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
834 | PCU03.INV3-BK-3_TS-0_TR15-TL0_S1 | 3-BK-3_TS-0_TR15-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
835 | PCU03.INV3-BK-3_TS-0_TR16-TL0_S0 | 3-BK-3_TS-0_TR16-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
836 | PCU03.INV3-BK-3_TS-0_TR16-TL0_S1 | 3-BK-3_TS-0_TR16-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
837 | PCU03.INV3-BK-3_TS-0_TR17-TL0_S0 | 3-BK-3_TS-0_TR17-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
838 | PCU03.INV3-BK-3_TS-0_TR17-TL0_S1 | 3-BK-3_TS-0_TR17-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
839 | PCU03.INV3-BK-3_TS-0_TR18-TL0_S0 | 3-BK-3_TS-0_TR18-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
840 | PCU03.INV3-BK-3_TS-0_TR18-TL0_S1 | 3-BK-3_TS-0_TR18-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
841 | PCU03.INV3-BK-3_TS-0_TR19-TL0_S0 | 3-BK-3_TS-0_TR19-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
842 | PCU03.INV3-BK-3_TS-0_TR19-TL0_S1 | 3-BK-3_TS-0_TR19-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
843 | PCU03.INV3-BK-3_TS-0_TR20-TL0_S0 | 3-BK-3_TS-0_TR20-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
844 | PCU03.INV3-BK-3_TS-0_TR20-TL0_S1 | 3-BK-3_TS-0_TR20-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
845 | PCU03.INV3-BK-3_TS-0_TR21-TL0_S0 | 3-BK-3_TS-0_TR21-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
846 | PCU03.INV3-BK-3_TS-0_TR21-TL0_S1 | 3-BK-3_TS-0_TR21-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
847 | PCU03.INV3-BK-3_TS-0_TR22-TL0_S1 | 3-BK-3_TS-0_TR22-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
848 | PCU03.INV4-BK-3_TS-0_TR22-TL0_S0 | 3-BK-3_TS-0_TR22-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
849 | PCU03.INV4-BK-3_TS-0_TR23-TL0_S0 | 3-BK-3_TS-0_TR23-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
850 | PCU03.INV4-BK-3_TS-0_TR23-TL0_S1 | 3-BK-3_TS-0_TR23-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
851 | PCU03.INV4-BK-3_TS-0_TR24-TL0_S0 | 3-BK-3_TS-0_TR24-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
852 | PCU03.INV4-BK-3_TS-0_TR24-TL0_S1 | 3-BK-3_TS-0_TR24-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
853 | PCU03.INV4-BK-3_TS-0_TR25-TL0_S0 | 3-BK-3_TS-0_TR25-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
854 | PCU03.INV4-BK-3_TS-0_TR25-TL0_S1 | 3-BK-3_TS-0_TR25-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
855 | PCU03.INV4-BK-3_TS-0_TR26-TL0_S0 | 3-BK-3_TS-0_TR26-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
856 | PCU03.INV4-BK-3_TS-0_TR26-TL0_S1 | 3-BK-3_TS-0_TR26-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
857 | PCU03.INV4-BK-3_TS-0_TR27-TL0_S0 | 3-BK-3_TS-0_TR27-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
858 | PCU03.INV4-BK-3_TS-0_TR27-TL0_S1 | 3-BK-3_TS-0_TR27-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
859 | PCU03.INV4-BK-3_TS-0_TR28-TL0_S0 | 3-BK-3_TS-0_TR28-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
860 | PCU03.INV4-BK-3_TS-0_TR28-TL0_S1 | 3-BK-3_TS-0_TR28-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
861 | PCU03.INV4-BK-3_TS-0_TR29-TL0_S0 | 3-BK-3_TS-0_TR29-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
862 | PCU03.INV4-BK-3_TS-0_TR29-TL0_S1 | 3-BK-3_TS-0_TR29-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
863 | PCU03.INV5-BK-3_TS-1_TR0-TL0_S0 | 3-BK-3_TS-1_TR0-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
864 | PCU03.INV5-BK-3_TS-1_TR0-TL0_S1 | 3-BK-3_TS-1_TR0-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
865 | PCU03.INV5-BK-3_TS-1_TR1-TL0_S0 | 3-BK-3_TS-1_TR1-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
866 | PCU03.INV5-BK-3_TS-1_TR1-TL0_S1 | 3-BK-3_TS-1_TR1-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
867 | PCU03.INV5-BK-3_TS-1_TR2-TL0_S0 | 3-BK-3_TS-1_TR2-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
868 | PCU03.INV5-BK-3_TS-1_TR2-TL0_S1 | 3-BK-3_TS-1_TR2-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
869 | PCU03.INV5-BK-3_TS-1_TR3-TL0_S0 | 3-BK-3_TS-1_TR3-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
870 | PCU03.INV5-BK-3_TS-1_TR3-TL0_S1 | 3-BK-3_TS-1_TR3-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
871 | PCU03.INV5-BK-3_TS-1_TR4-TL0_S0 | 3-BK-3_TS-1_TR4-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
872 | PCU03.INV5-BK-3_TS-1_TR4-TL0_S1 | 3-BK-3_TS-1_TR4-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
873 | PCU03.INV5-BK-3_TS-1_TR5-TL0_S0 | 3-BK-3_TS-1_TR5-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
874 | PCU03.INV5-BK-3_TS-1_TR5-TL0_S1 | 3-BK-3_TS-1_TR5-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
875 | PCU03.INV5-BK-3_TS-1_TR6-TL0_S0 | 3-BK-3_TS-1_TR6-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
876 | PCU03.INV5-BK-3_TS-1_TR6-TL0_S1 | 3-BK-3_TS-1_TR6-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
877 | PCU03.INV5-BK-3_TS-1_TR7-TL0_S0 | 3-BK-3_TS-1_TR7-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
878 | PCU03.INV5-BK-3_TS-1_TR7-TL0_S1 | 3-BK-3_TS-1_TR7-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
879 | PCU03.INV5-BK-3_TS-1_TR8-TL0_S0 | 3-BK-3_TS-1_TR8-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
880 | PCU03.INV5-BK-3_TS-1_TR8-TL0_S1 | 3-BK-3_TS-1_TR8-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
881 | PCU03.INV5-BK-3_TS-1_TR9-TL0_S0 | 3-BK-3_TS-1_TR9-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
882 | PCU03.INV5-BK-3_TS-1_TR9-TL0_S1 | 3-BK-3_TS-1_TR9-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
883 | PCU03.INV6-BK-3_TS-1_TR10-TL0_S0 | 3-BK-3_TS-1_TR10-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
884 | PCU03.INV6-BK-3_TS-1_TR10-TL0_S1 | 3-BK-3_TS-1_TR10-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
885 | PCU03.INV6-BK-3_TS-1_TR11-TL0_S0 | 3-BK-3_TS-1_TR11-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
886 | PCU03.INV6-BK-3_TS-1_TR11-TL0_S1 | 3-BK-3_TS-1_TR11-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
887 | PCU03.INV6-BK-3_TS-1_TR12-TL0_S0 | 3-BK-3_TS-1_TR12-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
888 | PCU03.INV6-BK-3_TS-1_TR12-TL0_S1 | 3-BK-3_TS-1_TR12-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
889 | PCU03.INV6-BK-3_TS-1_TR13-TL0_S0 | 3-BK-3_TS-1_TR13-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
890 | PCU03.INV6-BK-3_TS-1_TR13-TL0_S1 | 3-BK-3_TS-1_TR13-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
891 | PCU03.INV6-BK-3_TS-1_TR14-TL0_S0 | 3-BK-3_TS-1_TR14-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
892 | PCU03.INV6-BK-3_TS-1_TR14-TL0_S1 | 3-BK-3_TS-1_TR14-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
893 | PCU03.INV6-BK-3_TS-1_TR15-TL0_S0 | 3-BK-3_TS-1_TR15-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
894 | PCU03.INV6-BK-3_TS-1_TR15-TL0_S1 | 3-BK-3_TS-1_TR15-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
895 | PCU03.INV6-BK-3_TS-1_TR16-TL0_S0 | 3-BK-3_TS-1_TR16-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
896 | PCU03.INV6-BK-3_TS-1_TR16-TL0_S1 | 3-BK-3_TS-1_TR16-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
897 | PCU03.INV6-BK-3_TS-1_TR17-TL0_S0 | 3-BK-3_TS-1_TR17-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
898 | PCU03.INV6-BK-3_TS-1_TR17-TL0_S1 | 3-BK-3_TS-1_TR17-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
899 | PCU03.INV6-BK-3_TS-1_TR18-TL0_S0 | 3-BK-3_TS-1_TR18-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
900 | PCU03.INV6-BK-3_TS-1_TR18-TL0_S1 | 3-BK-3_TS-1_TR18-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
901 | PCU03.INV6-BK-3_TS-1_TR19-TL0_S0 | 3-BK-3_TS-1_TR19-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
902 | PCU03.INV6-BK-3_TS-1_TR19-TL0_S1 | 3-BK-3_TS-1_TR19-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
903 | PCU03.INV7-BK-3_TS-1_TR20-TL0_S0 | 3-BK-3_TS-1_TR20-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
904 | PCU03.INV7-BK-3_TS-1_TR20-TL0_S1 | 3-BK-3_TS-1_TR20-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
905 | PCU03.INV7-BK-3_TS-1_TR21-TL0_S0 | 3-BK-3_TS-1_TR21-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
906 | PCU03.INV7-BK-3_TS-1_TR21-TL0_S1 | 3-BK-3_TS-1_TR21-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
907 | PCU03.INV7-BK-3_TS-1_TR22-TL0_S0 | 3-BK-3_TS-1_TR22-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
908 | PCU03.INV7-BK-3_TS-1_TR22-TL0_S1 | 3-BK-3_TS-1_TR22-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
909 | PCU03.INV7-BK-3_TS-1_TR23-TL0_S0 | 3-BK-3_TS-1_TR23-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
910 | PCU03.INV7-BK-3_TS-1_TR23-TL0_S1 | 3-BK-3_TS-1_TR23-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
911 | PCU03.INV7-BK-3_TS-1_TR24-TL0_S0 | 3-BK-3_TS-1_TR24-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
912 | PCU03.INV7-BK-3_TS-1_TR24-TL0_S1 | 3-BK-3_TS-1_TR24-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
913 | PCU03.INV7-BK-3_TS-1_TR25-TL0_S0 | 3-BK-3_TS-1_TR25-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
914 | PCU03.INV7-BK-3_TS-1_TR25-TL0_S1 | 3-BK-3_TS-1_TR25-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
915 | PCU03.INV7-BK-3_TS-1_TR26-TL0_S0 | 3-BK-3_TS-1_TR26-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
916 | PCU03.INV7-BK-3_TS-1_TR26-TL0_S1 | 3-BK-3_TS-1_TR26-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
917 | PCU03.INV7-BK-3_TS-1_TR27-TL0_S0 | 3-BK-3_TS-1_TR27-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
918 | PCU03.INV7-BK-3_TS-1_TR27-TL0_S1 | 3-BK-3_TS-1_TR27-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
919 | PCU03.INV7-BK-3_TS-1_TR28-TL0_S0 | 3-BK-3_TS-1_TR28-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
920 | PCU03.INV7-BK-3_TS-1_TR28-TL0_S1 | 3-BK-3_TS-1_TR28-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
921 | PCU03.INV7-BK-3_TS-1_TR29-TL0_S0 | 3-BK-3_TS-1_TR29-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
922 | PCU03.INV7-BK-3_TS-1_TR29-TL0_S1 | 3-BK-3_TS-1_TR29-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
923 | PCU03.INV8-BK-3_TS-2_TR0-TL0_S0 | 3-BK-3_TS-2_TR0-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
924 | PCU03.INV8-BK-3_TS-2_TR0-TL0_S1 | 3-BK-3_TS-2_TR0-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
925 | PCU03.INV8-BK-3_TS-2_TR1-TL0_S0 | 3-BK-3_TS-2_TR1-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
926 | PCU03.INV8-BK-3_TS-2_TR1-TL0_S1 | 3-BK-3_TS-2_TR1-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
927 | PCU03.INV8-BK-3_TS-2_TR2-TL0_S0 | 3-BK-3_TS-2_TR2-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
928 | PCU03.INV8-BK-3_TS-2_TR2-TL0_S1 | 3-BK-3_TS-2_TR2-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
929 | PCU03.INV8-BK-3_TS-2_TR3-TL0_S0 | 3-BK-3_TS-2_TR3-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
930 | PCU03.INV8-BK-3_TS-2_TR3-TL0_S1 | 3-BK-3_TS-2_TR3-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
931 | PCU03.INV8-BK-3_TS-2_TR4-TL0_S0 | 3-BK-3_TS-2_TR4-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
932 | PCU03.INV8-BK-3_TS-2_TR4-TL0_S1 | 3-BK-3_TS-2_TR4-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
933 | PCU03.INV8-BK-3_TS-2_TR5-TL0_S0 | 3-BK-3_TS-2_TR5-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
934 | PCU03.INV8-BK-3_TS-2_TR5-TL0_S1 | 3-BK-3_TS-2_TR5-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
935 | PCU03.INV8-BK-3_TS-2_TR6-TL0_S0 | 3-BK-3_TS-2_TR6-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
936 | PCU03.INV8-BK-3_TS-2_TR6-TL0_S1 | 3-BK-3_TS-2_TR6-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
937 | PCU03.INV8-BK-3_TS-2_TR7-TL0_S0 | 3-BK-3_TS-2_TR7-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
938 | PCU03.INV8-BK-3_TS-2_TR7-TL0_S1 | 3-BK-3_TS-2_TR7-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
939 | PCU03.INV8-BK-3_TS-2_TR8-TL0_S0 | 3-BK-3_TS-2_TR8-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
940 | PCU03.INV8-BK-3_TS-2_TR8-TL0_S1 | 3-BK-3_TS-2_TR8-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
941 | PCU03.INV8-BK-3_TS-2_TR9-TL0_S0 | 3-BK-3_TS-2_TR9-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
942 | PCU03.INV8-BK-3_TS-2_TR9-TL0_S1 | 3-BK-3_TS-2_TR9-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
943 | PCU03.INV9-BK-3_TS-2_TR10-TL0_S0 | 3-BK-3_TS-2_TR10-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
944 | PCU03.INV9-BK-3_TS-2_TR10-TL0_S1 | 3-BK-3_TS-2_TR10-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
945 | PCU03.INV9-BK-3_TS-2_TR11-TL0_S0 | 3-BK-3_TS-2_TR11-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
946 | PCU03.INV9-BK-3_TS-2_TR11-TL0_S1 | 3-BK-3_TS-2_TR11-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
947 | PCU03.INV9-BK-3_TS-2_TR12-TL0_S0 | 3-BK-3_TS-2_TR12-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
948 | PCU03.INV9-BK-3_TS-2_TR12-TL0_S1 | 3-BK-3_TS-2_TR12-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
949 | PCU03.INV9-BK-3_TS-2_TR13-TL0_S0 | 3-BK-3_TS-2_TR13-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
950 | PCU03.INV9-BK-3_TS-2_TR13-TL0_S1 | 3-BK-3_TS-2_TR13-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
951 | PCU03.INV9-BK-3_TS-2_TR14-TL0_S0 | 3-BK-3_TS-2_TR14-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
952 | PCU03.INV9-BK-3_TS-2_TR14-TL0_S1 | 3-BK-3_TS-2_TR14-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
953 | PCU03.INV9-BK-3_TS-2_TR15-TL0_S0 | 3-BK-3_TS-2_TR15-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
954 | PCU03.INV9-BK-3_TS-2_TR15-TL0_S1 | 3-BK-3_TS-2_TR15-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
955 | PCU03.INV9-BK-3_TS-2_TR16-TL0_S0 | 3-BK-3_TS-2_TR16-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
956 | PCU03.INV9-BK-3_TS-2_TR16-TL0_S1 | 3-BK-3_TS-2_TR16-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
957 | PCU03.INV9-BK-3_TS-2_TR17-TL0_S0 | 3-BK-3_TS-2_TR17-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
958 | PCU03.INV9-BK-3_TS-2_TR17-TL0_S1 | 3-BK-3_TS-2_TR17-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
959 | PCU03.INV9-BK-3_TS-2_TR18-TL0_S0 | 3-BK-3_TS-2_TR18-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
960 | PCU03.INV9-BK-3_TS-2_TR18-TL0_S1 | 3-BK-3_TS-2_TR18-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
961 | PCU03.INV9-BK-3_TS-2_TR19-TL0_S0 | 3-BK-3_TS-2_TR19-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
962 | PCU03.INV9-BK-3_TS-2_TR19-TL0_S1 | 3-BK-3_TS-2_TR19-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
963 | PCU03.INV10-BK-3_TS-2_TR20-TL0_S0 | 3-BK-3_TS-2_TR20-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
964 | PCU03.INV10-BK-3_TS-2_TR20-TL0_S1 | 3-BK-3_TS-2_TR20-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
965 | PCU03.INV10-BK-3_TS-2_TR21-TL0_S0 | 3-BK-3_TS-2_TR21-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
966 | PCU03.INV10-BK-3_TS-2_TR21-TL0_S1 | 3-BK-3_TS-2_TR21-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
967 | PCU03.INV10-BK-3_TS-2_TR22-TL0_S0 | 3-BK-3_TS-2_TR22-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
968 | PCU03.INV10-BK-3_TS-2_TR22-TL0_S1 | 3-BK-3_TS-2_TR22-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
969 | PCU03.INV10-BK-3_TS-2_TR23-TL0_S0 | 3-BK-3_TS-2_TR23-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
970 | PCU03.INV10-BK-3_TS-2_TR23-TL0_S1 | 3-BK-3_TS-2_TR23-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
971 | PCU03.INV10-BK-3_TS-2_TR24-TL0_S0 | 3-BK-3_TS-2_TR24-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
972 | PCU03.INV10-BK-3_TS-2_TR24-TL0_S1 | 3-BK-3_TS-2_TR24-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
973 | PCU03.INV10-BK-3_TS-2_TR25-TL0_S0 | 3-BK-3_TS-2_TR25-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
974 | PCU03.INV10-BK-3_TS-2_TR25-TL0_S1 | 3-BK-3_TS-2_TR25-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
975 | PCU03.INV10-BK-3_TS-2_TR26-TL0_S0 | 3-BK-3_TS-2_TR26-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
976 | PCU03.INV10-BK-3_TS-2_TR26-TL0_S1 | 3-BK-3_TS-2_TR26-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
977 | PCU03.INV10-BK-3_TS-2_TR27-TL0_S0 | 3-BK-3_TS-2_TR27-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
978 | PCU03.INV10-BK-3_TS-2_TR27-TL0_S1 | 3-BK-3_TS-2_TR27-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
979 | PCU03.INV10-BK-3_TS-2_TR28-TL0_S0 | 3-BK-3_TS-2_TR28-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
980 | PCU03.INV10-BK-3_TS-2_TR28-TL0_S1 | 3-BK-3_TS-2_TR28-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
981 | PCU03.INV10-BK-3_TS-2_TR29-TL0_S0 | 3-BK-3_TS-2_TR29-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
982 | PCU03.INV10-BK-3_TS-2_TR29-TL0_S1 | 3-BK-3_TS-2_TR29-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
983 | PCU03.INV11-BK-3_TS-3_TR0-TL0_S0 | 3-BK-3_TS-3_TR0-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
984 | PCU03.INV11-BK-3_TS-3_TR0-TL0_S1 | 3-BK-3_TS-3_TR0-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
985 | PCU03.INV11-BK-3_TS-3_TR1-TL0_S0 | 3-BK-3_TS-3_TR1-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
986 | PCU03.INV11-BK-3_TS-3_TR1-TL0_S1 | 3-BK-3_TS-3_TR1-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
987 | PCU03.INV11-BK-3_TS-3_TR2-TL0_S0 | 3-BK-3_TS-3_TR2-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
988 | PCU03.INV11-BK-3_TS-3_TR2-TL0_S1 | 3-BK-3_TS-3_TR2-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
989 | PCU03.INV11-BK-3_TS-3_TR3-TL0_S0 | 3-BK-3_TS-3_TR3-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
990 | PCU03.INV11-BK-3_TS-3_TR3-TL0_S1 | 3-BK-3_TS-3_TR3-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
991 | PCU03.INV11-BK-3_TS-3_TR4-TL0_S0 | 3-BK-3_TS-3_TR4-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
992 | PCU03.INV11-BK-3_TS-3_TR4-TL0_S1 | 3-BK-3_TS-3_TR4-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
993 | PCU03.INV11-BK-3_TS-3_TR5-TL0_S0 | 3-BK-3_TS-3_TR5-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
994 | PCU03.INV11-BK-3_TS-3_TR5-TL0_S1 | 3-BK-3_TS-3_TR5-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
995 | PCU03.INV11-BK-3_TS-3_TR6-TL0_S0 | 3-BK-3_TS-3_TR6-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
996 | PCU03.INV11-BK-3_TS-3_TR6-TL0_S1 | 3-BK-3_TS-3_TR6-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
997 | PCU03.INV11-BK-3_TS-3_TR7-TL0_S0 | 3-BK-3_TS-3_TR7-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
998 | PCU03.INV11-BK-3_TS-3_TR7-TL0_S1 | 3-BK-3_TS-3_TR7-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
999 | PCU03.INV11-BK-3_TS-3_TR8-TL0_S0 | 3-BK-3_TS-3_TR8-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1000 | PCU03.INV11-BK-3_TS-3_TR8-TL0_S1 | 3-BK-3_TS-3_TR8-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1001 | PCU03.INV11-BK-3_TS-3_TR9-TL0_S0 | 3-BK-3_TS-3_TR9-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1002 | PCU03.INV11-BK-3_TS-3_TR9-TL0_S1 | 3-BK-3_TS-3_TR9-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1003 | PCU03.INV12-BK-3_TS-3_TR10-TL0_S0 | 3-BK-3_TS-3_TR10-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1004 | PCU03.INV12-BK-3_TS-3_TR10-TL0_S1 | 3-BK-3_TS-3_TR10-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1005 | PCU03.INV12-BK-3_TS-3_TR11-TL0_S0 | 3-BK-3_TS-3_TR11-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1006 | PCU03.INV12-BK-3_TS-3_TR11-TL0_S1 | 3-BK-3_TS-3_TR11-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1007 | PCU03.INV12-BK-3_TS-3_TR12-TL0_S0 | 3-BK-3_TS-3_TR12-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1008 | PCU03.INV12-BK-3_TS-3_TR12-TL0_S1 | 3-BK-3_TS-3_TR12-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1009 | PCU03.INV12-BK-3_TS-3_TR13-TL0_S0 | 3-BK-3_TS-3_TR13-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1010 | PCU03.INV12-BK-3_TS-3_TR13-TL0_S1 | 3-BK-3_TS-3_TR13-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1011 | PCU03.INV12-BK-3_TS-3_TR14-TL0_S0 | 3-BK-3_TS-3_TR14-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1012 | PCU03.INV12-BK-3_TS-3_TR14-TL0_S1 | 3-BK-3_TS-3_TR14-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1013 | PCU03.INV12-BK-3_TS-3_TR15-TL0_S0 | 3-BK-3_TS-3_TR15-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1014 | PCU03.INV12-BK-3_TS-3_TR15-TL0_S1 | 3-BK-3_TS-3_TR15-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1015 | PCU03.INV12-BK-3_TS-3_TR16-TL0_S0 | 3-BK-3_TS-3_TR16-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1016 | PCU03.INV12-BK-3_TS-3_TR16-TL0_S1 | 3-BK-3_TS-3_TR16-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1017 | PCU03.INV12-BK-3_TS-3_TR17-TL0_S0 | 3-BK-3_TS-3_TR17-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1018 | PCU03.INV12-BK-3_TS-3_TR17-TL0_S1 | 3-BK-3_TS-3_TR17-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1019 | PCU03.INV12-BK-3_TS-3_TR18-TL0_S0 | 3-BK-3_TS-3_TR18-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1020 | PCU03.INV12-BK-3_TS-3_TR18-TL0_S1 | 3-BK-3_TS-3_TR18-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1021 | PCU03.INV12-BK-3_TS-3_TR19-TL0_S0 | 3-BK-3_TS-3_TR19-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1022 | PCU03.INV12-BK-3_TS-3_TR19-TL0_S1 | 3-BK-3_TS-3_TR19-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1023 | PCU03.INV13-BK-3_TS-3_TR20-TL0_S0 | 3-BK-3_TS-3_TR20-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1024 | PCU03.INV13-BK-3_TS-3_TR20-TL0_S1 | 3-BK-3_TS-3_TR20-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1025 | PCU03.INV13-BK-3_TS-3_TR21-TL0_S0 | 3-BK-3_TS-3_TR21-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1026 | PCU03.INV13-BK-3_TS-3_TR21-TL0_S1 | 3-BK-3_TS-3_TR21-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1027 | PCU03.INV13-BK-3_TS-3_TR22-TL0_S0 | 3-BK-3_TS-3_TR22-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1028 | PCU03.INV13-BK-3_TS-3_TR22-TL0_S1 | 3-BK-3_TS-3_TR22-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1029 | PCU03.INV13-BK-3_TS-3_TR23-TL0_S0 | 3-BK-3_TS-3_TR23-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1030 | PCU03.INV13-BK-3_TS-3_TR23-TL0_S1 | 3-BK-3_TS-3_TR23-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1031 | PCU03.INV13-BK-3_TS-3_TR24-TL0_S0 | 3-BK-3_TS-3_TR24-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1032 | PCU03.INV13-BK-3_TS-3_TR24-TL0_S1 | 3-BK-3_TS-3_TR24-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1033 | PCU03.INV13-BK-3_TS-3_TR25-TL0_S0 | 3-BK-3_TS-3_TR25-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1034 | PCU03.INV13-BK-3_TS-3_TR25-TL0_S1 | 3-BK-3_TS-3_TR25-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1035 | PCU03.INV13-BK-3_TS-3_TR26-TL0_S0 | 3-BK-3_TS-3_TR26-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1036 | PCU03.INV13-BK-3_TS-3_TR26-TL0_S1 | 3-BK-3_TS-3_TR26-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1037 | PCU03.INV13-BK-3_TS-3_TR27-TL0_S0 | 3-BK-3_TS-3_TR27-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1038 | PCU03.INV13-BK-3_TS-3_TR27-TL0_S1 | 3-BK-3_TS-3_TR27-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1039 | PCU03.INV13-BK-3_TS-3_TR28-TL0_S0 | 3-BK-3_TS-3_TR28-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1040 | PCU03.INV13-BK-3_TS-3_TR28-TL0_S1 | 3-BK-3_TS-3_TR28-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1041 | PCU03.INV13-BK-3_TS-3_TR29-TL0_S0 | 3-BK-3_TS-3_TR29-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1042 | PCU03.INV13-BK-3_TS-3_TR29-TL0_S1 | 3-BK-3_TS-3_TR29-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1043 | PCU03.INV14-BK-3_TN-0_TR0-TL0_S0 | 3-BK-3_TN-0_TR0-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1044 | PCU03.INV14-BK-3_TN-0_TR0-TL0_S1 | 3-BK-3_TN-0_TR0-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1045 | PCU03.INV14-BK-3_TN-0_TR1-TL0_S0 | 3-BK-3_TN-0_TR1-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1046 | PCU03.INV14-BK-3_TN-0_TR1-TL0_S1 | 3-BK-3_TN-0_TR1-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1047 | PCU03.INV14-BK-3_TN-0_TR2-TL0_S0 | 3-BK-3_TN-0_TR2-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1048 | PCU03.INV14-BK-3_TN-0_TR2-TL0_S1 | 3-BK-3_TN-0_TR2-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1049 | PCU03.INV14-BK-3_TN-0_TR3-TL0_S0 | 3-BK-3_TN-0_TR3-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1050 | PCU03.INV14-BK-3_TN-0_TR3-TL0_S1 | 3-BK-3_TN-0_TR3-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1051 | PCU03.INV14-BK-3_TN-0_TR4-TL0_S0 | 3-BK-3_TN-0_TR4-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1052 | PCU03.INV14-BK-3_TN-0_TR4-TL0_S1 | 3-BK-3_TN-0_TR4-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1053 | PCU03.INV14-BK-3_TN-0_TR5-TL0_S0 | 3-BK-3_TN-0_TR5-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1054 | PCU03.INV14-BK-3_TN-0_TR5-TL0_S1 | 3-BK-3_TN-0_TR5-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1055 | PCU03.INV14-BK-3_TN-0_TR6-TL0_S0 | 3-BK-3_TN-0_TR6-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1056 | PCU03.INV14-BK-3_TN-0_TR6-TL0_S1 | 3-BK-3_TN-0_TR6-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1057 | PCU03.INV14-BK-3_TN-0_TR7-TL0_S0 | 3-BK-3_TN-0_TR7-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1058 | PCU03.INV15-BK-3_TN-0_TR7-TL0_S1 | 3-BK-3_TN-0_TR7-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1059 | PCU03.INV15-BK-3_TN-0_TR8-TL0_S0 | 3-BK-3_TN-0_TR8-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1060 | PCU03.INV15-BK-3_TN-0_TR8-TL0_S1 | 3-BK-3_TN-0_TR8-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1061 | PCU03.INV15-BK-3_TN-0_TR9-TL0_S0 | 3-BK-3_TN-0_TR9-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1062 | PCU03.INV15-BK-3_TN-0_TR9-TL0_S1 | 3-BK-3_TN-0_TR9-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1063 | PCU03.INV15-BK-3_TN-0_TR10-TL0_S0 | 3-BK-3_TN-0_TR10-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1064 | PCU03.INV15-BK-3_TN-0_TR10-TL0_S1 | 3-BK-3_TN-0_TR10-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1065 | PCU03.INV15-BK-3_TN-0_TR11-TL0_S0 | 3-BK-3_TN-0_TR11-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1066 | PCU03.INV15-BK-3_TN-0_TR11-TL0_S1 | 3-BK-3_TN-0_TR11-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1067 | PCU03.INV15-BK-3_TN-0_TR12-TL0_S0 | 3-BK-3_TN-0_TR12-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1068 | PCU03.INV15-BK-3_TN-0_TR12-TL0_S1 | 3-BK-3_TN-0_TR12-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1069 | PCU03.INV15-BK-3_TN-0_TR13-TL0_S0 | 3-BK-3_TN-0_TR13-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1070 | PCU03.INV15-BK-3_TN-0_TR13-TL0_S1 | 3-BK-3_TN-0_TR13-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1071 | PCU03.INV15-BK-3_TN-0_TR14-TL0_S0 | 3-BK-3_TN-0_TR14-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1072 | PCU03.INV15-BK-3_TN-0_TR14-TL0_S1 | 3-BK-3_TN-0_TR14-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1073 | PCU03.INV16-BK-3_TN-0_TR15-TL0_S0 | 3-BK-3_TN-0_TR15-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1074 | PCU03.INV16-BK-3_TN-0_TR15-TL0_S1 | 3-BK-3_TN-0_TR15-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1075 | PCU03.INV16-BK-3_TN-0_TR16-TL0_S0 | 3-BK-3_TN-0_TR16-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1076 | PCU03.INV16-BK-3_TN-0_TR16-TL0_S1 | 3-BK-3_TN-0_TR16-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1077 | PCU03.INV16-BK-3_TN-0_TR17-TL0_S0 | 3-BK-3_TN-0_TR17-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1078 | PCU03.INV16-BK-3_TN-0_TR17-TL0_S1 | 3-BK-3_TN-0_TR17-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1079 | PCU03.INV16-BK-3_TN-0_TR18-TL0_S0 | 3-BK-3_TN-0_TR18-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1080 | PCU03.INV16-BK-3_TN-0_TR18-TL0_S1 | 3-BK-3_TN-0_TR18-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1081 | PCU03.INV16-BK-3_TN-0_TR19-TL0_S0 | 3-BK-3_TN-0_TR19-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1082 | PCU03.INV16-BK-3_TN-0_TR19-TL0_S1 | 3-BK-3_TN-0_TR19-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1083 | PCU03.INV16-BK-3_TN-0_TR20-TL0_S0 | 3-BK-3_TN-0_TR20-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1084 | PCU03.INV16-BK-3_TN-0_TR20-TL0_S1 | 3-BK-3_TN-0_TR20-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1085 | PCU03.INV16-BK-3_TN-0_TR21-TL0_S0 | 3-BK-3_TN-0_TR21-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1086 | PCU03.INV16-BK-3_TN-0_TR21-TL0_S1 | 3-BK-3_TN-0_TR21-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1087 | PCU03.INV16-BK-3_TN-0_TR22-TL0_S0 | 3-BK-3_TN-0_TR22-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1088 | PCU03.INV17-BK-3_TN-0_TR22-TL0_S1 | 3-BK-3_TN-0_TR22-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1089 | PCU03.INV17-BK-3_TN-0_TR23-TL0_S0 | 3-BK-3_TN-0_TR23-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1090 | PCU03.INV17-BK-3_TN-0_TR23-TL0_S1 | 3-BK-3_TN-0_TR23-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1091 | PCU03.INV17-BK-3_TN-0_TR24-TL0_S0 | 3-BK-3_TN-0_TR24-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1092 | PCU03.INV17-BK-3_TN-0_TR24-TL0_S1 | 3-BK-3_TN-0_TR24-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1093 | PCU03.INV17-BK-3_TN-0_TR25-TL0_S0 | 3-BK-3_TN-0_TR25-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1094 | PCU03.INV17-BK-3_TN-0_TR25-TL0_S1 | 3-BK-3_TN-0_TR25-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1095 | PCU03.INV17-BK-3_TN-0_TR26-TL0_S0 | 3-BK-3_TN-0_TR26-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1096 | PCU03.INV17-BK-3_TN-0_TR26-TL0_S1 | 3-BK-3_TN-0_TR26-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1097 | PCU03.INV17-BK-3_TN-0_TR27-TL0_S0 | 3-BK-3_TN-0_TR27-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1098 | PCU03.INV17-BK-3_TN-0_TR27-TL0_S1 | 3-BK-3_TN-0_TR27-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1099 | PCU03.INV17-BK-3_TN-0_TR28-TL0_S0 | 3-BK-3_TN-0_TR28-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1100 | PCU03.INV17-BK-3_TN-0_TR28-TL0_S1 | 3-BK-3_TN-0_TR28-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1101 | PCU03.INV17-BK-3_TN-0_TR29-TL0_S0 | 3-BK-3_TN-0_TR29-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1102 | PCU03.INV17-BK-3_TN-0_TR29-TL0_S1 | 3-BK-3_TN-0_TR29-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1103 | PCU03.INV18-BK-3_TN-1_TR0-TL0_S0 | 3-BK-3_TN-1_TR0-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1104 | PCU03.INV18-BK-3_TN-1_TR0-TL0_S1 | 3-BK-3_TN-1_TR0-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1105 | PCU03.INV18-BK-3_TN-1_TR1-TL0_S0 | 3-BK-3_TN-1_TR1-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1106 | PCU03.INV18-BK-3_TN-1_TR1-TL0_S1 | 3-BK-3_TN-1_TR1-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1107 | PCU03.INV18-BK-3_TN-1_TR2-TL0_S0 | 3-BK-3_TN-1_TR2-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1108 | PCU03.INV18-BK-3_TN-1_TR2-TL0_S1 | 3-BK-3_TN-1_TR2-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1109 | PCU03.INV18-BK-3_TN-1_TR3-TL0_S0 | 3-BK-3_TN-1_TR3-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1110 | PCU03.INV18-BK-3_TN-1_TR3-TL0_S1 | 3-BK-3_TN-1_TR3-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1111 | PCU03.INV18-BK-3_TN-1_TR4-TL0_S0 | 3-BK-3_TN-1_TR4-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1112 | PCU03.INV18-BK-3_TN-1_TR4-TL0_S1 | 3-BK-3_TN-1_TR4-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1113 | PCU03.INV18-BK-3_TN-1_TR5-TL0_S0 | 3-BK-3_TN-1_TR5-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1114 | PCU03.INV18-BK-3_TN-1_TR5-TL0_S1 | 3-BK-3_TN-1_TR5-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1115 | PCU03.INV18-BK-3_TN-1_TR6-TL0_S0 | 3-BK-3_TN-1_TR6-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1116 | PCU03.INV18-BK-3_TN-1_TR6-TL0_S1 | 3-BK-3_TN-1_TR6-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1117 | PCU03.INV18-BK-3_TN-1_TR7-TL0_S0 | 3-BK-3_TN-1_TR7-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1118 | PCU03.INV18-BK-3_TN-1_TR7-TL0_S1 | 3-BK-3_TN-1_TR7-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1119 | PCU03.INV18-BK-3_TN-1_TR8-TL0_S0 | 3-BK-3_TN-1_TR8-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1120 | PCU03.INV18-BK-3_TN-1_TR8-TL0_S1 | 3-BK-3_TN-1_TR8-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1121 | PCU03.INV18-BK-3_TN-1_TR9-TL0_S0 | 3-BK-3_TN-1_TR9-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1122 | PCU03.INV18-BK-3_TN-1_TR9-TL0_S1 | 3-BK-3_TN-1_TR9-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1123 | PCU03.INV19-BK-3_TN-1_TR10-TL0_S0 | 3-BK-3_TN-1_TR10-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1124 | PCU03.INV19-BK-3_TN-1_TR10-TL0_S1 | 3-BK-3_TN-1_TR10-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1125 | PCU03.INV19-BK-3_TN-1_TR11-TL0_S0 | 3-BK-3_TN-1_TR11-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1126 | PCU03.INV19-BK-3_TN-1_TR11-TL0_S1 | 3-BK-3_TN-1_TR11-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1127 | PCU03.INV19-BK-3_TN-1_TR12-TL0_S0 | 3-BK-3_TN-1_TR12-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1128 | PCU03.INV19-BK-3_TN-1_TR12-TL0_S1 | 3-BK-3_TN-1_TR12-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1129 | PCU03.INV19-BK-3_TN-1_TR13-TL0_S0 | 3-BK-3_TN-1_TR13-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1130 | PCU03.INV19-BK-3_TN-1_TR13-TL0_S1 | 3-BK-3_TN-1_TR13-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1131 | PCU03.INV19-BK-3_TN-1_TR14-TL0_S0 | 3-BK-3_TN-1_TR14-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1132 | PCU03.INV19-BK-3_TN-1_TR14-TL0_S1 | 3-BK-3_TN-1_TR14-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1133 | PCU03.INV19-BK-3_TN-1_TR15-TL0_S0 | 3-BK-3_TN-1_TR15-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1134 | PCU03.INV19-BK-3_TN-1_TR15-TL0_S1 | 3-BK-3_TN-1_TR15-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1135 | PCU03.INV19-BK-3_TN-1_TR16-TL0_S0 | 3-BK-3_TN-1_TR16-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1136 | PCU03.INV19-BK-3_TN-1_TR16-TL0_S1 | 3-BK-3_TN-1_TR16-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1137 | PCU03.INV19-BK-3_TN-1_TR17-TL0_S0 | 3-BK-3_TN-1_TR17-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1138 | PCU03.INV19-BK-3_TN-1_TR17-TL0_S1 | 3-BK-3_TN-1_TR17-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1139 | PCU03.INV19-BK-3_TN-1_TR18-TL0_S0 | 3-BK-3_TN-1_TR18-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1140 | PCU03.INV19-BK-3_TN-1_TR18-TL0_S1 | 3-BK-3_TN-1_TR18-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1141 | PCU03.INV19-BK-3_TN-1_TR19-TL0_S0 | 3-BK-3_TN-1_TR19-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1142 | PCU03.INV19-BK-3_TN-1_TR19-TL0_S1 | 3-BK-3_TN-1_TR19-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1143 | PCU03.INV20-BK-3_TN-1_TR20-TL0_S0 | 3-BK-3_TN-1_TR20-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1144 | PCU03.INV20-BK-3_TN-1_TR20-TL0_S1 | 3-BK-3_TN-1_TR20-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1145 | PCU03.INV20-BK-3_TN-1_TR21-TL0_S0 | 3-BK-3_TN-1_TR21-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1146 | PCU03.INV20-BK-3_TN-1_TR21-TL0_S1 | 3-BK-3_TN-1_TR21-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1147 | PCU03.INV20-BK-3_TN-1_TR22-TL0_S0 | 3-BK-3_TN-1_TR22-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1148 | PCU03.INV20-BK-3_TN-1_TR22-TL0_S1 | 3-BK-3_TN-1_TR22-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1149 | PCU03.INV20-BK-3_TN-1_TR23-TL0_S0 | 3-BK-3_TN-1_TR23-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1150 | PCU03.INV20-BK-3_TN-1_TR23-TL0_S1 | 3-BK-3_TN-1_TR23-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1151 | PCU03.INV20-BK-3_TN-1_TR24-TL0_S0 | 3-BK-3_TN-1_TR24-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1152 | PCU03.INV20-BK-3_TN-1_TR24-TL0_S1 | 3-BK-3_TN-1_TR24-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1153 | PCU03.INV20-BK-3_TN-1_TR25-TL0_S0 | 3-BK-3_TN-1_TR25-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1154 | PCU03.INV20-BK-3_TN-1_TR25-TL0_S1 | 3-BK-3_TN-1_TR25-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1155 | PCU03.INV20-BK-3_TN-1_TR26-TL0_S0 | 3-BK-3_TN-1_TR26-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1156 | PCU03.INV20-BK-3_TN-1_TR26-TL0_S1 | 3-BK-3_TN-1_TR26-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1157 | PCU03.INV20-BK-3_TN-1_TR27-TL0_S0 | 3-BK-3_TN-1_TR27-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1158 | PCU03.INV20-BK-3_TN-1_TR27-TL0_S1 | 3-BK-3_TN-1_TR27-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1159 | PCU03.INV20-BK-3_TN-1_TR28-TL0_S0 | 3-BK-3_TN-1_TR28-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1160 | PCU03.INV20-BK-3_TN-1_TR28-TL0_S1 | 3-BK-3_TN-1_TR28-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1161 | PCU03.INV20-BK-3_TN-1_TR29-TL0_S0 | 3-BK-3_TN-1_TR29-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1162 | PCU03.INV20-BK-3_TN-1_TR29-TL0_S1 | 3-BK-3_TN-1_TR29-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 3 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1163 | PCU04.INV1-BK-4_TS-0_TR0-TL0_S0 | 4-BK-4_TS-0_TR0-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1164 | PCU04.INV1-BK-4_TS-0_TR0-TL0_S1 | 4-BK-4_TS-0_TR0-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1165 | PCU04.INV1-BK-4_TS-0_TR1-TL0_S0 | 4-BK-4_TS-0_TR1-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1166 | PCU04.INV1-BK-4_TS-0_TR1-TL0_S1 | 4-BK-4_TS-0_TR1-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1167 | PCU04.INV1-BK-4_TS-0_TR2-TL0_S0 | 4-BK-4_TS-0_TR2-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1168 | PCU04.INV1-BK-4_TS-0_TR2-TL0_S1 | 4-BK-4_TS-0_TR2-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1169 | PCU04.INV1-BK-4_TS-0_TR3-TL0_S0 | 4-BK-4_TS-0_TR3-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1170 | PCU04.INV1-BK-4_TS-0_TR3-TL0_S1 | 4-BK-4_TS-0_TR3-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1171 | PCU04.INV1-BK-4_TS-0_TR4-TL0_S0 | 4-BK-4_TS-0_TR4-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1172 | PCU04.INV1-BK-4_TS-0_TR4-TL0_S1 | 4-BK-4_TS-0_TR4-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1173 | PCU04.INV1-BK-4_TS-0_TR5-TL0_S0 | 4-BK-4_TS-0_TR5-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1174 | PCU04.INV1-BK-4_TS-0_TR5-TL0_S1 | 4-BK-4_TS-0_TR5-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1175 | PCU04.INV1-BK-4_TS-0_TR6-TL0_S0 | 4-BK-4_TS-0_TR6-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1176 | PCU04.INV1-BK-4_TS-0_TR6-TL0_S1 | 4-BK-4_TS-0_TR6-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1177 | PCU04.INV1-BK-4_TS-0_TR7-TL0_S0 | 4-BK-4_TS-0_TR7-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1178 | PCU04.INV1-BK-4_TS-0_TR7-TL0_S1 | 4-BK-4_TS-0_TR7-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1179 | PCU04.INV1-BK-4_TS-0_TR8-TL0_S0 | 4-BK-4_TS-0_TR8-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1180 | PCU04.INV1-BK-4_TS-0_TR8-TL0_S1 | 4-BK-4_TS-0_TR8-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1181 | PCU04.INV1-BK-4_TS-0_TR9-TL0_S0 | 4-BK-4_TS-0_TR9-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1182 | PCU04.INV1-BK-4_TS-0_TR9-TL0_S1 | 4-BK-4_TS-0_TR9-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1183 | PCU04.INV1-BK-4_TS-0_TR10-TL0_S0 | 4-BK-4_TS-0_TR10-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1184 | PCU04.INV1-BK-4_TS-0_TR10-TL0_S1 | 4-BK-4_TS-0_TR10-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1185 | PCU04.INV2-BK-4_TS-0_TR11-TL0_S0 | 4-BK-4_TS-0_TR11-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1186 | PCU04.INV2-BK-4_TS-0_TR11-TL0_S1 | 4-BK-4_TS-0_TR11-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1187 | PCU04.INV2-BK-4_TS-0_TR12-TL0_S0 | 4-BK-4_TS-0_TR12-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1188 | PCU04.INV2-BK-4_TS-0_TR12-TL0_S1 | 4-BK-4_TS-0_TR12-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1189 | PCU04.INV2-BK-4_TS-0_TR13-TL0_S0 | 4-BK-4_TS-0_TR13-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1190 | PCU04.INV2-BK-4_TS-0_TR13-TL0_S1 | 4-BK-4_TS-0_TR13-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1191 | PCU04.INV2-BK-4_TS-0_TR14-TL0_S0 | 4-BK-4_TS-0_TR14-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1192 | PCU04.INV2-BK-4_TS-0_TR14-TL0_S1 | 4-BK-4_TS-0_TR14-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1193 | PCU04.INV2-BK-4_TS-0_TR15-TL0_S0 | 4-BK-4_TS-0_TR15-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1194 | PCU04.INV2-BK-4_TS-0_TR15-TL0_S1 | 4-BK-4_TS-0_TR15-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1195 | PCU04.INV2-BK-4_TS-0_TR16-TL0_S0 | 4-BK-4_TS-0_TR16-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1196 | PCU04.INV2-BK-4_TS-0_TR16-TL0_S1 | 4-BK-4_TS-0_TR16-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1197 | PCU04.INV2-BK-4_TS-0_TR17-TL0_S0 | 4-BK-4_TS-0_TR17-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1198 | PCU04.INV2-BK-4_TS-0_TR17-TL0_S1 | 4-BK-4_TS-0_TR17-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1199 | PCU04.INV2-BK-4_TS-0_TR18-TL0_S0 | 4-BK-4_TS-0_TR18-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1200 | PCU04.INV2-BK-4_TS-0_TR18-TL0_S1 | 4-BK-4_TS-0_TR18-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1201 | PCU04.INV2-BK-4_TS-0_TR19-TL0_S0 | 4-BK-4_TS-0_TR19-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1202 | PCU04.INV2-BK-4_TS-0_TR19-TL0_S1 | 4-BK-4_TS-0_TR19-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1203 | PCU04.INV2-BK-4_TS-0_TR20-TL0_S0 | 4-BK-4_TS-0_TR20-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1204 | PCU04.INV2-BK-4_TS-0_TR20-TL0_S1 | 4-BK-4_TS-0_TR20-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1205 | PCU04.INV2-BK-4_TS-0_TR21-TL0_S0 | 4-BK-4_TS-0_TR21-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1206 | PCU04.INV2-BK-4_TS-0_TR21-TL0_S1 | 4-BK-4_TS-0_TR21-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1207 | PCU04.INV3-BK-4_TS-0_TR22-TL0_S0 | 4-BK-4_TS-0_TR22-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1208 | PCU04.INV3-BK-4_TS-0_TR22-TL0_S1 | 4-BK-4_TS-0_TR22-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1209 | PCU04.INV3-BK-4_TS-0_TR23-TL0_S0 | 4-BK-4_TS-0_TR23-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1210 | PCU04.INV3-BK-4_TS-0_TR23-TL0_S1 | 4-BK-4_TS-0_TR23-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1211 | PCU04.INV3-BK-4_TS-0_TR24-TL0_S0 | 4-BK-4_TS-0_TR24-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1212 | PCU04.INV3-BK-4_TS-0_TR24-TL0_S1 | 4-BK-4_TS-0_TR24-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1213 | PCU04.INV3-BK-4_TS-0_TR25-TL0_S0 | 4-BK-4_TS-0_TR25-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1214 | PCU04.INV3-BK-4_TS-0_TR25-TL0_S1 | 4-BK-4_TS-0_TR25-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1215 | PCU04.INV3-BK-4_TS-0_TR26-TL0_S0 | 4-BK-4_TS-0_TR26-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1216 | PCU04.INV3-BK-4_TS-0_TR26-TL0_S1 | 4-BK-4_TS-0_TR26-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1217 | PCU04.INV3-BK-4_TS-0_TR27-TL0_S0 | 4-BK-4_TS-0_TR27-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1218 | PCU04.INV3-BK-4_TS-0_TR27-TL0_S1 | 4-BK-4_TS-0_TR27-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1219 | PCU04.INV3-BK-4_TS-0_TR28-TL0_S0 | 4-BK-4_TS-0_TR28-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1220 | PCU04.INV3-BK-4_TS-0_TR28-TL0_S1 | 4-BK-4_TS-0_TR28-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1221 | PCU04.INV3-BK-4_TS-0_TR29-TL0_S0 | 4-BK-4_TS-0_TR29-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1222 | PCU04.INV3-BK-4_TS-0_TR29-TL0_S1 | 4-BK-4_TS-0_TR29-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1223 | PCU04.INV3-BK-4_TS-0_TR30-TL0_S0 | 4-BK-4_TS-0_TR30-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1224 | PCU04.INV3-BK-4_TS-0_TR30-TL0_S1 | 4-BK-4_TS-0_TR30-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1225 | PCU04.INV3-BK-4_TS-0_TR31-TL0_S0 | 4-BK-4_TS-0_TR31-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1226 | PCU04.INV3-BK-4_TS-0_TR31-TL0_S1 | 4-BK-4_TS-0_TR31-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1227 | PCU04.INV3-BK-4_TS-0_TR32-TL0_S0 | 4-BK-4_TS-0_TR32-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1228 | PCU04.INV3-BK-4_TS-0_TR32-TL0_S1 | 4-BK-4_TS-0_TR32-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1229 | PCU04.INV4-BK-4_TS-1_TR0-TL0_S0 | 4-BK-4_TS-1_TR0-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1230 | PCU04.INV4-BK-4_TS-1_TR0-TL0_S1 | 4-BK-4_TS-1_TR0-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1231 | PCU04.INV4-BK-4_TS-1_TR1-TL0_S0 | 4-BK-4_TS-1_TR1-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1232 | PCU04.INV4-BK-4_TS-1_TR1-TL0_S1 | 4-BK-4_TS-1_TR1-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1233 | PCU04.INV4-BK-4_TS-1_TR2-TL0_S0 | 4-BK-4_TS-1_TR2-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1234 | PCU04.INV4-BK-4_TS-1_TR2-TL0_S1 | 4-BK-4_TS-1_TR2-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1235 | PCU04.INV4-BK-4_TS-1_TR3-TL0_S0 | 4-BK-4_TS-1_TR3-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1236 | PCU04.INV4-BK-4_TS-1_TR3-TL0_S1 | 4-BK-4_TS-1_TR3-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1237 | PCU04.INV4-BK-4_TS-1_TR4-TL0_S0 | 4-BK-4_TS-1_TR4-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1238 | PCU04.INV4-BK-4_TS-1_TR4-TL0_S1 | 4-BK-4_TS-1_TR4-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1239 | PCU04.INV4-BK-4_TS-1_TR5-TL0_S0 | 4-BK-4_TS-1_TR5-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1240 | PCU04.INV4-BK-4_TS-1_TR5-TL0_S1 | 4-BK-4_TS-1_TR5-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1241 | PCU04.INV4-BK-4_TS-1_TR6-TL0_S0 | 4-BK-4_TS-1_TR6-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1242 | PCU04.INV4-BK-4_TS-1_TR6-TL0_S1 | 4-BK-4_TS-1_TR6-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1243 | PCU04.INV4-BK-4_TS-1_TR7-TL0_S0 | 4-BK-4_TS-1_TR7-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1244 | PCU04.INV4-BK-4_TS-1_TR7-TL0_S1 | 4-BK-4_TS-1_TR7-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1245 | PCU04.INV4-BK-4_TS-1_TR8-TL0_S0 | 4-BK-4_TS-1_TR8-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1246 | PCU04.INV4-BK-4_TS-1_TR8-TL0_S1 | 4-BK-4_TS-1_TR8-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1247 | PCU04.INV4-BK-4_TS-1_TR9-TL0_S0 | 4-BK-4_TS-1_TR9-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1248 | PCU04.INV4-BK-4_TS-1_TR9-TL0_S1 | 4-BK-4_TS-1_TR9-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1249 | PCU04.INV4-BK-4_TS-1_TR10-TL0_S0 | 4-BK-4_TS-1_TR10-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1250 | PCU04.INV4-BK-4_TS-1_TR10-TL0_S1 | 4-BK-4_TS-1_TR10-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1251 | PCU04.INV4-BK-4_TS-1_TR11-TL0_S1 | 4-BK-4_TS-1_TR11-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1252 | PCU04.INV5-BK-4_TS-1_TR21-TL0_S0 | 4-BK-4_TS-1_TR21-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1253 | PCU04.INV5-BK-4_TS-1_TR22-TL0_S0 | 4-BK-4_TS-1_TR22-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1254 | PCU04.INV5-BK-4_TS-1_TR22-TL0_S1 | 4-BK-4_TS-1_TR22-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1255 | PCU04.INV5-BK-4_TS-1_TR23-TL0_S0 | 4-BK-4_TS-1_TR23-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1256 | PCU04.INV5-BK-4_TS-1_TR23-TL0_S1 | 4-BK-4_TS-1_TR23-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1257 | PCU04.INV5-BK-4_TS-1_TR24-TL0_S0 | 4-BK-4_TS-1_TR24-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1258 | PCU04.INV5-BK-4_TS-1_TR24-TL0_S1 | 4-BK-4_TS-1_TR24-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1259 | PCU04.INV5-BK-4_TS-1_TR25-TL0_S0 | 4-BK-4_TS-1_TR25-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1260 | PCU04.INV5-BK-4_TS-1_TR25-TL0_S1 | 4-BK-4_TS-1_TR25-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1261 | PCU04.INV5-BK-4_TS-1_TR26-TL0_S0 | 4-BK-4_TS-1_TR26-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1262 | PCU04.INV5-BK-4_TS-1_TR26-TL0_S1 | 4-BK-4_TS-1_TR26-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1263 | PCU04.INV5-BK-4_TS-1_TR27-TL0_S0 | 4-BK-4_TS-1_TR27-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1264 | PCU04.INV5-BK-4_TS-1_TR27-TL0_S1 | 4-BK-4_TS-1_TR27-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1265 | PCU04.INV5-BK-4_TS-1_TR28-TL0_S0 | 4-BK-4_TS-1_TR28-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1266 | PCU04.INV5-BK-4_TS-1_TR28-TL0_S1 | 4-BK-4_TS-1_TR28-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1267 | PCU04.INV5-BK-4_TS-1_TR29-TL0_S0 | 4-BK-4_TS-1_TR29-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1268 | PCU04.INV5-BK-4_TS-1_TR29-TL0_S1 | 4-BK-4_TS-1_TR29-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1269 | PCU04.INV5-BK-4_TS-1_TR30-TL0_S0 | 4-BK-4_TS-1_TR30-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1270 | PCU04.INV5-BK-4_TS-1_TR30-TL0_S1 | 4-BK-4_TS-1_TR30-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1271 | PCU04.INV5-BK-4_TS-1_TR31-TL0_S0 | 4-BK-4_TS-1_TR31-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1272 | PCU04.INV5-BK-4_TS-1_TR31-TL0_S1 | 4-BK-4_TS-1_TR31-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1273 | PCU04.INV5-BK-4_TS-1_TR32-TL0_S0 | 4-BK-4_TS-1_TR32-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1274 | PCU04.INV5-BK-4_TS-1_TR32-TL0_S1 | 4-BK-4_TS-1_TR32-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1275 | PCU04.INV6-BK-4_TS-2_TR0-TL0_S0 | 4-BK-4_TS-2_TR0-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1276 | PCU04.INV6-BK-4_TS-2_TR0-TL0_S1 | 4-BK-4_TS-2_TR0-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1277 | PCU04.INV6-BK-4_TS-2_TR1-TL0_S0 | 4-BK-4_TS-2_TR1-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1278 | PCU04.INV6-BK-4_TS-2_TR1-TL0_S1 | 4-BK-4_TS-2_TR1-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1279 | PCU04.INV6-BK-4_TS-2_TR2-TL0_S0 | 4-BK-4_TS-2_TR2-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1280 | PCU04.INV6-BK-4_TS-2_TR2-TL0_S1 | 4-BK-4_TS-2_TR2-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1281 | PCU04.INV6-BK-4_TS-2_TR3-TL0_S0 | 4-BK-4_TS-2_TR3-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1282 | PCU04.INV6-BK-4_TS-2_TR3-TL0_S1 | 4-BK-4_TS-2_TR3-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1283 | PCU04.INV6-BK-4_TS-2_TR4-TL0_S0 | 4-BK-4_TS-2_TR4-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1284 | PCU04.INV6-BK-4_TS-2_TR4-TL0_S1 | 4-BK-4_TS-2_TR4-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1285 | PCU04.INV6-BK-4_TS-2_TR5-TL0_S0 | 4-BK-4_TS-2_TR5-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1286 | PCU04.INV6-BK-4_TS-2_TR5-TL0_S1 | 4-BK-4_TS-2_TR5-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1287 | PCU04.INV6-BK-4_TS-2_TR6-TL0_S0 | 4-BK-4_TS-2_TR6-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1288 | PCU04.INV6-BK-4_TS-2_TR6-TL0_S1 | 4-BK-4_TS-2_TR6-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1289 | PCU04.INV6-BK-4_TS-2_TR7-TL0_S0 | 4-BK-4_TS-2_TR7-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1290 | PCU04.INV6-BK-4_TS-2_TR7-TL0_S1 | 4-BK-4_TS-2_TR7-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1291 | PCU04.INV6-BK-4_TS-2_TR8-TL0_S0 | 4-BK-4_TS-2_TR8-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1292 | PCU04.INV6-BK-4_TS-2_TR8-TL0_S1 | 4-BK-4_TS-2_TR8-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1293 | PCU04.INV6-BK-4_TS-2_TR9-TL0_S0 | 4-BK-4_TS-2_TR9-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1294 | PCU04.INV6-BK-4_TS-2_TR9-TL0_S1 | 4-BK-4_TS-2_TR9-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1295 | PCU04.INV6-BK-4_TS-2_TR10-TL0_S0 | 4-BK-4_TS-2_TR10-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1296 | PCU04.INV6-BK-4_TS-2_TR10-TL0_S1 | 4-BK-4_TS-2_TR10-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1297 | PCU04.INV6-BK-4_TS-2_TR11-TL0_S1 | 4-BK-4_TS-2_TR11-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1298 | PCU04.INV7-BK-4_TS-2_TR16-TL0_S0 | 4-BK-4_TS-2_TR16-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1299 | PCU04.INV7-BK-4_TS-2_TR17-TL0_S0 | 4-BK-4_TS-2_TR17-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1300 | PCU04.INV7-BK-4_TS-2_TR17-TL0_S1 | 4-BK-4_TS-2_TR17-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1301 | PCU04.INV7-BK-4_TS-2_TR18-TL0_S0 | 4-BK-4_TS-2_TR18-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1302 | PCU04.INV7-BK-4_TS-2_TR18-TL0_S1 | 4-BK-4_TS-2_TR18-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1303 | PCU04.INV7-BK-4_TS-2_TR19-TL0_S0 | 4-BK-4_TS-2_TR19-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1304 | PCU04.INV7-BK-4_TS-2_TR19-TL0_S1 | 4-BK-4_TS-2_TR19-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1305 | PCU04.INV7-BK-4_TS-2_TR20-TL0_S0 | 4-BK-4_TS-2_TR20-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1306 | PCU04.INV7-BK-4_TS-2_TR20-TL0_S1 | 4-BK-4_TS-2_TR20-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1307 | PCU04.INV7-BK-4_TS-2_TR21-TL0_S0 | 4-BK-4_TS-2_TR21-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1308 | PCU04.INV7-BK-4_TS-2_TR21-TL0_S1 | 4-BK-4_TS-2_TR21-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1309 | PCU04.INV7-BK-4_TS-2_TR22-TL0_S0 | 4-BK-4_TS-2_TR22-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1310 | PCU04.INV7-BK-4_TS-2_TR22-TL0_S1 | 4-BK-4_TS-2_TR22-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1311 | PCU04.INV7-BK-4_TS-2_TR23-TL0_S0 | 4-BK-4_TS-2_TR23-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1312 | PCU04.INV7-BK-4_TS-2_TR23-TL0_S1 | 4-BK-4_TS-2_TR23-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1313 | PCU04.INV7-BK-4_TS-2_TR24-TL0_S0 | 4-BK-4_TS-2_TR24-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1314 | PCU04.INV7-BK-4_TS-2_TR24-TL0_S1 | 4-BK-4_TS-2_TR24-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1315 | PCU04.INV7-BK-4_TS-2_TR25-TL0_S0 | 4-BK-4_TS-2_TR25-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1316 | PCU04.INV7-BK-4_TS-2_TR25-TL0_S1 | 4-BK-4_TS-2_TR25-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1317 | PCU04.INV7-BK-4_TS-2_TR26-TL0_S0 | 4-BK-4_TS-2_TR26-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1318 | PCU04.INV7-BK-4_TS-2_TR26-TL0_S1 | 4-BK-4_TS-2_TR26-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1319 | PCU04.INV7-BK-4_TS-2_TR27-TL0_S0 | 4-BK-4_TS-2_TR27-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1320 | PCU04.INV7-BK-4_TS-2_TR27-TL0_S1 | 4-BK-4_TS-2_TR27-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1321 | PCU04.INV8-BK-4_TS-3_TR0-TL0_S0 | 4-BK-4_TS-3_TR0-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1322 | PCU04.INV8-BK-4_TS-3_TR0-TL0_S1 | 4-BK-4_TS-3_TR0-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1323 | PCU04.INV8-BK-4_TS-3_TR1-TL0_S0 | 4-BK-4_TS-3_TR1-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1324 | PCU04.INV8-BK-4_TS-3_TR1-TL0_S1 | 4-BK-4_TS-3_TR1-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1325 | PCU04.INV8-BK-4_TS-3_TR2-TL0_S0 | 4-BK-4_TS-3_TR2-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1326 | PCU04.INV8-BK-4_TS-3_TR2-TL0_S1 | 4-BK-4_TS-3_TR2-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1327 | PCU04.INV8-BK-4_TS-3_TR3-TL0_S0 | 4-BK-4_TS-3_TR3-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1328 | PCU04.INV8-BK-4_TS-3_TR3-TL0_S1 | 4-BK-4_TS-3_TR3-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1329 | PCU04.INV8-BK-4_TS-3_TR4-TL0_S0 | 4-BK-4_TS-3_TR4-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1330 | PCU04.INV8-BK-4_TS-3_TR4-TL0_S1 | 4-BK-4_TS-3_TR4-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1331 | PCU04.INV8-BK-4_TS-3_TR5-TL0_S0 | 4-BK-4_TS-3_TR5-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1332 | PCU04.INV8-BK-4_TS-3_TR5-TL0_S1 | 4-BK-4_TS-3_TR5-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1333 | PCU04.INV8-BK-4_TS-3_TR6-TL0_S0 | 4-BK-4_TS-3_TR6-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1334 | PCU04.INV8-BK-4_TS-3_TR6-TL0_S1 | 4-BK-4_TS-3_TR6-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1335 | PCU04.INV8-BK-4_TS-3_TR7-TL0_S0 | 4-BK-4_TS-3_TR7-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1336 | PCU04.INV8-BK-4_TS-3_TR7-TL0_S1 | 4-BK-4_TS-3_TR7-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1337 | PCU04.INV8-BK-4_TS-3_TR8-TL0_S0 | 4-BK-4_TS-3_TR8-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1338 | PCU04.INV8-BK-4_TS-3_TR8-TL0_S1 | 4-BK-4_TS-3_TR8-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1339 | PCU04.INV8-BK-4_TS-3_TR9-TL0_S0 | 4-BK-4_TS-3_TR9-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1340 | PCU04.INV8-BK-4_TS-3_TR9-TL0_S1 | 4-BK-4_TS-3_TR9-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1341 | PCU04.INV8-BK-4_TS-3_TR10-TL0_S0 | 4-BK-4_TS-3_TR10-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1342 | PCU04.INV8-BK-4_TS-3_TR10-TL0_S1 | 4-BK-4_TS-3_TR10-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1343 | PCU04.INV9-BK-4_TS-1_TR11-TL0_S0 | 4-BK-4_TS-1_TR11-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 130.3 | 65.15 | 65.15 | 26.28 | 1061.2 | 17.31 | 0 | 9.75 | 9.75 | 0.92 | 168.76 | 0.92
1344 | PCU04.INV9-BK-4_TS-1_TR12-TL0_S0 | 4-BK-4_TS-1_TR12-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 120.2 | 60.1 | 60.1 | 21.28 | 1061.2 | 17.31 | 0 | 8.99 | 8.99 | 0.85 | 155.68 | 0.85
1345 | PCU04.INV9-BK-4_TS-1_TR12-TL0_S1 | 4-BK-4_TS-1_TR12-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 195.03 | 97.51 | 97.51 | 21.28 | 1061.2 | 17.31 | 0 | 14.59 | 14.59 | 1.38 | 252.6 | 1.38
1346 | PCU04.INV9-BK-4_TS-1_TR13-TL0_S0 | 4-BK-4_TS-1_TR13-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 110.1 | 55.05 | 55.05 | 16.28 | 1061.2 | 17.31 | 0 | 8.24 | 8.24 | 0.78 | 142.6 | 0.78
1347 | PCU04.INV9-BK-4_TS-1_TR13-TL0_S1 | 4-BK-4_TS-1_TR13-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 184.93 | 92.46 | 92.46 | 16.28 | 1061.2 | 17.31 | 0 | 13.84 | 13.84 | 1.3 | 239.52 | 1.31
1348 | PCU04.INV9-BK-4_TS-1_TR14-TL0_S0 | 4-BK-4_TS-1_TR14-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 100 | 50 | 50 | 11.28 | 1061.2 | 17.31 | 0 | 7.48 | 7.48 | 0.71 | 129.52 | 0.71
1349 | PCU04.INV9-BK-4_TS-1_TR14-TL0_S1 | 4-BK-4_TS-1_TR14-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 174.83 | 87.41 | 87.41 | 11.28 | 1061.2 | 17.31 | 0 | 13.08 | 13.08 | 1.23 | 226.44 | 1.23
1350 | PCU04.INV9-BK-4_TS-1_TR15-TL0_S0 | 4-BK-4_TS-1_TR15-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 89.9 | 44.95 | 44.95 | 6.28 | 1061.2 | 17.31 | 0 | 6.73 | 6.73 | 0.63 | 116.43 | 0.63
1351 | PCU04.INV9-BK-4_TS-1_TR15-TL0_S1 | 4-BK-4_TS-1_TR15-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 164.73 | 82.36 | 82.36 | 6.28 | 1061.2 | 17.31 | 0 | 12.33 | 12.33 | 1.16 | 213.35 | 1.16
1352 | PCU04.INV9-BK-4_TS-1_TR16-TL0_S0 | 4-BK-4_TS-1_TR16-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 100 | 50 | 50 | 11.28 | 1061.2 | 17.31 | 0 | 7.48 | 7.48 | 0.71 | 129.52 | 0.71
1353 | PCU04.INV9-BK-4_TS-1_TR16-TL0_S1 | 4-BK-4_TS-1_TR16-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 174.83 | 87.41 | 87.41 | 11.28 | 1061.2 | 17.31 | 0 | 13.08 | 13.08 | 1.23 | 226.44 | 1.23
1354 | PCU04.INV9-BK-4_TS-1_TR17-TL0_S0 | 4-BK-4_TS-1_TR17-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 110.1 | 55.05 | 55.05 | 16.28 | 1061.2 | 17.31 | 0 | 8.24 | 8.24 | 0.78 | 142.6 | 0.78
1355 | PCU04.INV9-BK-4_TS-1_TR17-TL0_S1 | 4-BK-4_TS-1_TR17-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 184.93 | 92.46 | 92.46 | 16.28 | 1061.2 | 17.31 | 0 | 13.84 | 13.84 | 1.3 | 239.52 | 1.31
1356 | PCU04.INV9-BK-4_TS-1_TR18-TL0_S0 | 4-BK-4_TS-1_TR18-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 120.2 | 60.1 | 60.1 | 21.28 | 1061.2 | 17.31 | 0 | 8.99 | 8.99 | 0.85 | 155.68 | 0.85
1357 | PCU04.INV9-BK-4_TS-1_TR18-TL0_S1 | 4-BK-4_TS-1_TR18-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 195.03 | 97.51 | 97.51 | 21.28 | 1061.2 | 17.31 | 0 | 14.59 | 14.59 | 1.38 | 252.6 | 1.38
1358 | PCU04.INV9-BK-4_TS-1_TR19-TL0_S0 | 4-BK-4_TS-1_TR19-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 130.3 | 65.15 | 65.15 | 26.28 | 1061.2 | 17.31 | 0 | 9.75 | 9.75 | 0.92 | 168.76 | 0.92
1359 | PCU04.INV9-BK-4_TS-1_TR19-TL0_S1 | 4-BK-4_TS-1_TR19-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 205.13 | 102.56 | 102.56 | 26.28 | 1061.2 | 17.31 | 0 | 15.35 | 15.35 | 1.45 | 265.68 | 1.45
1360 | PCU04.INV9-BK-4_TS-1_TR20-TL0_S0 | 4-BK-4_TS-1_TR20-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 140.4 | 70.2 | 70.2 | 31.28 | 1061.2 | 17.31 | 0 | 10.5 | 10.5 | 0.99 | 181.84 | 0.99
1361 | PCU04.INV9-BK-4_TS-1_TR20-TL0_S1 | 4-BK-4_TS-1_TR20-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 215.23 | 107.61 | 107.61 | 31.28 | 1061.2 | 17.31 | 0 | 16.1 | 16.1 | 1.52 | 278.76 | 1.52
1362 | PCU04.INV9-BK-4_TS-1_TR21-TL0_S1 | 4-BK-4_TS-1_TR21-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 225.33 | 112.66 | 112.66 | 36.28 | 1061.2 | 17.31 | 0 | 16.86 | 16.86 | 1.59 | 291.84 | 1.59
1363 | PCU04.INV9-BK-4_TS-2_TR15-TL0_S0 | 4-BK-4_TS-2_TR15-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1364 | PCU04.INV9-BK-4_TS-2_TR15-TL0_S1 | 4-BK-4_TS-2_TR15-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1365 | PCU04.INV9-BK-4_TS-2_TR16-TL0_S1 | 4-BK-4_TS-2_TR16-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1366 | PCU04.INV10-BK-4_TS-2_TR11-TL0_S0 | 4-BK-4_TS-2_TR11-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 150.5 | 75.25 | 75.25 | 36.28 | 1061.2 | 17.31 | 0 | 11.26 | 11.26 | 1.06 | 194.92 | 1.06
1367 | PCU04.INV10-BK-4_TS-2_TR12-TL0_S0 | 4-BK-4_TS-2_TR12-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 140.4 | 70.2 | 70.2 | 31.28 | 1061.2 | 17.31 | 0 | 10.5 | 10.5 | 0.99 | 181.84 | 0.99
1368 | PCU04.INV10-BK-4_TS-2_TR12-TL0_S1 | 4-BK-4_TS-2_TR12-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 215.23 | 107.61 | 107.61 | 31.28 | 1061.2 | 17.31 | 0 | 16.1 | 16.1 | 1.52 | 278.76 | 1.52
1369 | PCU04.INV10-BK-4_TS-2_TR13-TL0_S0 | 4-BK-4_TS-2_TR13-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 130.3 | 65.15 | 65.15 | 26.28 | 1061.2 | 17.31 | 0 | 9.75 | 9.75 | 0.92 | 168.76 | 0.92
1370 | PCU04.INV10-BK-4_TS-2_TR13-TL0_S1 | 4-BK-4_TS-2_TR13-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 205.13 | 102.56 | 102.56 | 26.28 | 1061.2 | 17.31 | 0 | 15.35 | 15.35 | 1.45 | 265.68 | 1.45
1371 | PCU04.INV10-BK-4_TS-2_TR14-TL0_S0 | 4-BK-4_TS-2_TR14-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 120.2 | 60.1 | 60.1 | 21.28 | 1061.2 | 17.31 | 0 | 8.99 | 8.99 | 0.85 | 155.68 | 0.85
1372 | PCU04.INV10-BK-4_TS-2_TR14-TL0_S1 | 4-BK-4_TS-2_TR14-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 195.03 | 97.51 | 97.51 | 21.28 | 1061.2 | 17.31 | 0 | 14.59 | 14.59 | 1.38 | 252.6 | 1.38
1373 | PCU04.INV10-BK-4_TS-3_TR11-TL0_S0 | 4-BK-4_TS-3_TR11-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1374 | PCU04.INV10-BK-4_TS-3_TR11-TL0_S1 | 4-BK-4_TS-3_TR11-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1375 | PCU04.INV10-BK-4_TS-3_TR12-TL0_S0 | 4-BK-4_TS-3_TR12-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1376 | PCU04.INV10-BK-4_TS-3_TR12-TL0_S1 | 4-BK-4_TS-3_TR12-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1377 | PCU04.INV10-BK-4_TS-3_TR13-TL0_S0 | 4-BK-4_TS-3_TR13-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1378 | PCU04.INV10-BK-4_TS-3_TR13-TL0_S1 | 4-BK-4_TS-3_TR13-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1379 | PCU04.INV10-BK-4_TS-3_TR14-TL0_S0 | 4-BK-4_TS-3_TR14-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1380 | PCU04.INV10-BK-4_TS-3_TR14-TL0_S1 | 4-BK-4_TS-3_TR14-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1381 | PCU04.INV10-BK-4_TS-3_TR15-TL0_S0 | 4-BK-4_TS-3_TR15-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1382 | PCU04.INV10-BK-4_TS-3_TR15-TL0_S1 | 4-BK-4_TS-3_TR15-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1383 | PCU04.INV10-BK-4_TS-3_TR16-TL0_S0 | 4-BK-4_TS-3_TR16-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1384 | PCU04.INV10-BK-4_TS-3_TR16-TL0_S1 | 4-BK-4_TS-3_TR16-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1385 | PCU04.INV10-BK-4_TS-3_TR17-TL0_S0 | 4-BK-4_TS-3_TR17-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1386 | PCU04.INV10-BK-4_TS-3_TR17-TL0_S1 | 4-BK-4_TS-3_TR17-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1387 | PCU04.INV10-BK-4_TS-3_TR18-TL0_S0 | 4-BK-4_TS-3_TR18-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1388 | PCU04.INV10-BK-4_TS-3_TR18-TL0_S1 | 4-BK-4_TS-3_TR18-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1389 | PCU04.INV11-BK-4_TN-0_TR0-TL0_S0 | 4-BK-4_TN-0_TR0-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1390 | PCU04.INV11-BK-4_TN-0_TR0-TL0_S1 | 4-BK-4_TN-0_TR0-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1391 | PCU04.INV11-BK-4_TN-0_TR1-TL0_S0 | 4-BK-4_TN-0_TR1-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1392 | PCU04.INV11-BK-4_TN-0_TR1-TL0_S1 | 4-BK-4_TN-0_TR1-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1393 | PCU04.INV11-BK-4_TN-0_TR2-TL0_S0 | 4-BK-4_TN-0_TR2-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1394 | PCU04.INV11-BK-4_TN-0_TR2-TL0_S1 | 4-BK-4_TN-0_TR2-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1395 | PCU04.INV11-BK-4_TN-0_TR3-TL0_S0 | 4-BK-4_TN-0_TR3-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1396 | PCU04.INV11-BK-4_TN-0_TR3-TL0_S1 | 4-BK-4_TN-0_TR3-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1397 | PCU04.INV11-BK-4_TN-0_TR4-TL0_S0 | 4-BK-4_TN-0_TR4-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1398 | PCU04.INV11-BK-4_TN-0_TR4-TL0_S1 | 4-BK-4_TN-0_TR4-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1399 | PCU04.INV11-BK-4_TN-0_TR5-TL0_S0 | 4-BK-4_TN-0_TR5-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1400 | PCU04.INV11-BK-4_TN-0_TR5-TL0_S1 | 4-BK-4_TN-0_TR5-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1401 | PCU04.INV11-BK-4_TN-0_TR6-TL0_S0 | 4-BK-4_TN-0_TR6-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1402 | PCU04.INV11-BK-4_TN-0_TR6-TL0_S1 | 4-BK-4_TN-0_TR6-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1403 | PCU04.INV11-BK-4_TN-0_TR7-TL0_S0 | 4-BK-4_TN-0_TR7-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1404 | PCU04.INV11-BK-4_TN-0_TR7-TL0_S1 | 4-BK-4_TN-0_TR7-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1405 | PCU04.INV11-BK-4_TN-0_TR8-TL0_S0 | 4-BK-4_TN-0_TR8-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1406 | PCU04.INV11-BK-4_TN-0_TR8-TL0_S1 | 4-BK-4_TN-0_TR8-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1407 | PCU04.INV11-BK-4_TN-0_TR9-TL0_S0 | 4-BK-4_TN-0_TR9-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1408 | PCU04.INV11-BK-4_TN-0_TR9-TL0_S1 | 4-BK-4_TN-0_TR9-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1409 | PCU04.INV11-BK-4_TN-0_TR10-TL0_S0 | 4-BK-4_TN-0_TR10-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1410 | PCU04.INV11-BK-4_TN-0_TR10-TL0_S1 | 4-BK-4_TN-0_TR10-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1411 | PCU04.INV12-BK-4_TN-0_TR11-TL0_S0 | 4-BK-4_TN-0_TR11-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1412 | PCU04.INV12-BK-4_TN-0_TR11-TL0_S1 | 4-BK-4_TN-0_TR11-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1413 | PCU04.INV12-BK-4_TN-0_TR12-TL0_S0 | 4-BK-4_TN-0_TR12-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1414 | PCU04.INV12-BK-4_TN-0_TR12-TL0_S1 | 4-BK-4_TN-0_TR12-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1415 | PCU04.INV12-BK-4_TN-0_TR13-TL0_S0 | 4-BK-4_TN-0_TR13-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1416 | PCU04.INV12-BK-4_TN-0_TR13-TL0_S1 | 4-BK-4_TN-0_TR13-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1417 | PCU04.INV12-BK-4_TN-0_TR14-TL0_S0 | 4-BK-4_TN-0_TR14-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1418 | PCU04.INV12-BK-4_TN-0_TR14-TL0_S1 | 4-BK-4_TN-0_TR14-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1419 | PCU04.INV12-BK-4_TN-0_TR15-TL0_S0 | 4-BK-4_TN-0_TR15-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1420 | PCU04.INV12-BK-4_TN-0_TR15-TL0_S1 | 4-BK-4_TN-0_TR15-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1421 | PCU04.INV12-BK-4_TN-0_TR16-TL0_S0 | 4-BK-4_TN-0_TR16-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1422 | PCU04.INV12-BK-4_TN-0_TR16-TL0_S1 | 4-BK-4_TN-0_TR16-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1423 | PCU04.INV12-BK-4_TN-0_TR17-TL0_S0 | 4-BK-4_TN-0_TR17-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1424 | PCU04.INV12-BK-4_TN-0_TR17-TL0_S1 | 4-BK-4_TN-0_TR17-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1425 | PCU04.INV12-BK-4_TN-0_TR18-TL0_S0 | 4-BK-4_TN-0_TR18-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1426 | PCU04.INV12-BK-4_TN-0_TR18-TL0_S1 | 4-BK-4_TN-0_TR18-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1427 | PCU04.INV12-BK-4_TN-0_TR19-TL0_S0 | 4-BK-4_TN-0_TR19-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1428 | PCU04.INV12-BK-4_TN-0_TR19-TL0_S1 | 4-BK-4_TN-0_TR19-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1429 | PCU04.INV12-BK-4_TN-0_TR20-TL0_S0 | 4-BK-4_TN-0_TR20-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1430 | PCU04.INV12-BK-4_TN-0_TR20-TL0_S1 | 4-BK-4_TN-0_TR20-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1431 | PCU04.INV12-BK-4_TN-0_TR21-TL0_S0 | 4-BK-4_TN-0_TR21-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1432 | PCU04.INV12-BK-4_TN-0_TR21-TL0_S1 | 4-BK-4_TN-0_TR21-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1433 | PCU04.INV13-BK-4_TN-0_TR22-TL0_S0 | 4-BK-4_TN-0_TR22-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1434 | PCU04.INV13-BK-4_TN-0_TR22-TL0_S1 | 4-BK-4_TN-0_TR22-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1435 | PCU04.INV13-BK-4_TN-0_TR23-TL0_S0 | 4-BK-4_TN-0_TR23-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1436 | PCU04.INV13-BK-4_TN-0_TR23-TL0_S1 | 4-BK-4_TN-0_TR23-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1437 | PCU04.INV13-BK-4_TN-0_TR24-TL0_S0 | 4-BK-4_TN-0_TR24-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1438 | PCU04.INV13-BK-4_TN-0_TR24-TL0_S1 | 4-BK-4_TN-0_TR24-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1439 | PCU04.INV13-BK-4_TN-0_TR25-TL0_S0 | 4-BK-4_TN-0_TR25-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1440 | PCU04.INV13-BK-4_TN-0_TR25-TL0_S1 | 4-BK-4_TN-0_TR25-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1441 | PCU04.INV13-BK-4_TN-0_TR26-TL0_S0 | 4-BK-4_TN-0_TR26-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1442 | PCU04.INV13-BK-4_TN-0_TR26-TL0_S1 | 4-BK-4_TN-0_TR26-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1443 | PCU04.INV13-BK-4_TN-0_TR27-TL0_S0 | 4-BK-4_TN-0_TR27-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1444 | PCU04.INV13-BK-4_TN-0_TR27-TL0_S1 | 4-BK-4_TN-0_TR27-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1445 | PCU04.INV13-BK-4_TN-0_TR28-TL0_S0 | 4-BK-4_TN-0_TR28-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1446 | PCU04.INV13-BK-4_TN-0_TR28-TL0_S1 | 4-BK-4_TN-0_TR28-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1447 | PCU04.INV13-BK-4_TN-0_TR29-TL0_S0 | 4-BK-4_TN-0_TR29-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1448 | PCU04.INV13-BK-4_TN-0_TR29-TL0_S1 | 4-BK-4_TN-0_TR29-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1449 | PCU04.INV13-BK-4_TN-0_TR30-TL0_S0 | 4-BK-4_TN-0_TR30-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1450 | PCU04.INV13-BK-4_TN-0_TR30-TL0_S1 | 4-BK-4_TN-0_TR30-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1451 | PCU04.INV13-BK-4_TN-0_TR31-TL0_S0 | 4-BK-4_TN-0_TR31-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1452 | PCU04.INV13-BK-4_TN-0_TR31-TL0_S1 | 4-BK-4_TN-0_TR31-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1453 | PCU04.INV13-BK-4_TN-0_TR32-TL0_S0 | 4-BK-4_TN-0_TR32-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1454 | PCU04.INV13-BK-4_TN-0_TR32-TL0_S1 | 4-BK-4_TN-0_TR32-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1455 | PCU04.INV14-BK-4_TN-1_TR0-TL0_S0 | 4-BK-4_TN-1_TR0-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1456 | PCU04.INV14-BK-4_TN-1_TR0-TL0_S1 | 4-BK-4_TN-1_TR0-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1457 | PCU04.INV14-BK-4_TN-1_TR1-TL0_S0 | 4-BK-4_TN-1_TR1-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1458 | PCU04.INV14-BK-4_TN-1_TR1-TL0_S1 | 4-BK-4_TN-1_TR1-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1459 | PCU04.INV14-BK-4_TN-1_TR2-TL0_S0 | 4-BK-4_TN-1_TR2-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1460 | PCU04.INV14-BK-4_TN-1_TR2-TL0_S1 | 4-BK-4_TN-1_TR2-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1461 | PCU04.INV14-BK-4_TN-1_TR3-TL0_S0 | 4-BK-4_TN-1_TR3-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1462 | PCU04.INV14-BK-4_TN-1_TR3-TL0_S1 | 4-BK-4_TN-1_TR3-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1463 | PCU04.INV14-BK-4_TN-1_TR4-TL0_S0 | 4-BK-4_TN-1_TR4-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1464 | PCU04.INV14-BK-4_TN-1_TR4-TL0_S1 | 4-BK-4_TN-1_TR4-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1465 | PCU04.INV14-BK-4_TN-1_TR5-TL0_S0 | 4-BK-4_TN-1_TR5-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1466 | PCU04.INV14-BK-4_TN-1_TR5-TL0_S1 | 4-BK-4_TN-1_TR5-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1467 | PCU04.INV14-BK-4_TN-1_TR6-TL0_S0 | 4-BK-4_TN-1_TR6-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1468 | PCU04.INV14-BK-4_TN-1_TR6-TL0_S1 | 4-BK-4_TN-1_TR6-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1469 | PCU04.INV14-BK-4_TN-1_TR7-TL0_S0 | 4-BK-4_TN-1_TR7-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1470 | PCU04.INV14-BK-4_TN-1_TR7-TL0_S1 | 4-BK-4_TN-1_TR7-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1471 | PCU04.INV14-BK-4_TN-1_TR8-TL0_S0 | 4-BK-4_TN-1_TR8-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1472 | PCU04.INV14-BK-4_TN-1_TR8-TL0_S1 | 4-BK-4_TN-1_TR8-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1473 | PCU04.INV14-BK-4_TN-1_TR9-TL0_S0 | 4-BK-4_TN-1_TR9-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1474 | PCU04.INV14-BK-4_TN-1_TR9-TL0_S1 | 4-BK-4_TN-1_TR9-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1475 | PCU04.INV14-BK-4_TN-1_TR10-TL0_S0 | 4-BK-4_TN-1_TR10-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1476 | PCU04.INV14-BK-4_TN-1_TR10-TL0_S1 | 4-BK-4_TN-1_TR10-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1477 | PCU04.INV15-BK-4_TN-1_TR11-TL0_S0 | 4-BK-4_TN-1_TR11-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1478 | PCU04.INV15-BK-4_TN-1_TR11-TL0_S1 | 4-BK-4_TN-1_TR11-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1479 | PCU04.INV15-BK-4_TN-1_TR12-TL0_S0 | 4-BK-4_TN-1_TR12-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1480 | PCU04.INV15-BK-4_TN-1_TR12-TL0_S1 | 4-BK-4_TN-1_TR12-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1481 | PCU04.INV15-BK-4_TN-1_TR13-TL0_S0 | 4-BK-4_TN-1_TR13-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1482 | PCU04.INV15-BK-4_TN-1_TR13-TL0_S1 | 4-BK-4_TN-1_TR13-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1483 | PCU04.INV15-BK-4_TN-1_TR14-TL0_S0 | 4-BK-4_TN-1_TR14-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1484 | PCU04.INV15-BK-4_TN-1_TR14-TL0_S1 | 4-BK-4_TN-1_TR14-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1485 | PCU04.INV15-BK-4_TN-1_TR15-TL0_S0 | 4-BK-4_TN-1_TR15-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1486 | PCU04.INV15-BK-4_TN-1_TR15-TL0_S1 | 4-BK-4_TN-1_TR15-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1487 | PCU04.INV15-BK-4_TN-1_TR16-TL0_S0 | 4-BK-4_TN-1_TR16-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1488 | PCU04.INV15-BK-4_TN-1_TR16-TL0_S1 | 4-BK-4_TN-1_TR16-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1489 | PCU04.INV15-BK-4_TN-1_TR17-TL0_S0 | 4-BK-4_TN-1_TR17-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1490 | PCU04.INV15-BK-4_TN-1_TR17-TL0_S1 | 4-BK-4_TN-1_TR17-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1491 | PCU04.INV15-BK-4_TN-1_TR18-TL0_S0 | 4-BK-4_TN-1_TR18-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1492 | PCU04.INV15-BK-4_TN-1_TR18-TL0_S1 | 4-BK-4_TN-1_TR18-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1493 | PCU04.INV15-BK-4_TN-1_TR19-TL0_S0 | 4-BK-4_TN-1_TR19-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1494 | PCU04.INV15-BK-4_TN-1_TR19-TL0_S1 | 4-BK-4_TN-1_TR19-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1495 | PCU04.INV15-BK-4_TN-1_TR20-TL0_S0 | 4-BK-4_TN-1_TR20-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1496 | PCU04.INV15-BK-4_TN-1_TR20-TL0_S1 | 4-BK-4_TN-1_TR20-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1497 | PCU04.INV15-BK-4_TN-1_TR21-TL0_S0 | 4-BK-4_TN-1_TR21-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1498 | PCU04.INV15-BK-4_TN-1_TR21-TL0_S1 | 4-BK-4_TN-1_TR21-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1499 | PCU04.INV16-BK-4_TN-1_TR22-TL0_S0 | 4-BK-4_TN-1_TR22-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1500 | PCU04.INV16-BK-4_TN-1_TR22-TL0_S1 | 4-BK-4_TN-1_TR22-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1501 | PCU04.INV16-BK-4_TN-1_TR23-TL0_S0 | 4-BK-4_TN-1_TR23-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1502 | PCU04.INV16-BK-4_TN-1_TR23-TL0_S1 | 4-BK-4_TN-1_TR23-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1503 | PCU04.INV16-BK-4_TN-1_TR24-TL0_S0 | 4-BK-4_TN-1_TR24-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1504 | PCU04.INV16-BK-4_TN-1_TR24-TL0_S1 | 4-BK-4_TN-1_TR24-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1505 | PCU04.INV16-BK-4_TN-1_TR25-TL0_S0 | 4-BK-4_TN-1_TR25-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1506 | PCU04.INV16-BK-4_TN-1_TR25-TL0_S1 | 4-BK-4_TN-1_TR25-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1507 | PCU04.INV16-BK-4_TN-1_TR26-TL0_S0 | 4-BK-4_TN-1_TR26-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1508 | PCU04.INV16-BK-4_TN-1_TR26-TL0_S1 | 4-BK-4_TN-1_TR26-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1509 | PCU04.INV16-BK-4_TN-1_TR27-TL0_S0 | 4-BK-4_TN-1_TR27-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1510 | PCU04.INV16-BK-4_TN-1_TR27-TL0_S1 | 4-BK-4_TN-1_TR27-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1511 | PCU04.INV16-BK-4_TN-1_TR28-TL0_S0 | 4-BK-4_TN-1_TR28-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1512 | PCU04.INV16-BK-4_TN-1_TR28-TL0_S1 | 4-BK-4_TN-1_TR28-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1513 | PCU04.INV16-BK-4_TN-1_TR29-TL0_S0 | 4-BK-4_TN-1_TR29-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1514 | PCU04.INV16-BK-4_TN-1_TR29-TL0_S1 | 4-BK-4_TN-1_TR29-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1515 | PCU04.INV16-BK-4_TN-1_TR30-TL0_S0 | 4-BK-4_TN-1_TR30-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1516 | PCU04.INV16-BK-4_TN-1_TR30-TL0_S1 | 4-BK-4_TN-1_TR30-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1517 | PCU04.INV16-BK-4_TN-1_TR31-TL0_S0 | 4-BK-4_TN-1_TR31-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1518 | PCU04.INV16-BK-4_TN-1_TR31-TL0_S1 | 4-BK-4_TN-1_TR31-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1519 | PCU04.INV16-BK-4_TN-1_TR32-TL0_S0 | 4-BK-4_TN-1_TR32-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1520 | PCU04.INV16-BK-4_TN-1_TR32-TL0_S1 | 4-BK-4_TN-1_TR32-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1521 | PCU04.INV17-BK-4_TN-2_TR0-TL0_S0 | 4-BK-4_TN-2_TR0-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1522 | PCU04.INV17-BK-4_TN-2_TR0-TL0_S1 | 4-BK-4_TN-2_TR0-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1523 | PCU04.INV17-BK-4_TN-2_TR1-TL0_S0 | 4-BK-4_TN-2_TR1-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1524 | PCU04.INV17-BK-4_TN-2_TR1-TL0_S1 | 4-BK-4_TN-2_TR1-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1525 | PCU04.INV17-BK-4_TN-2_TR2-TL0_S0 | 4-BK-4_TN-2_TR2-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1526 | PCU04.INV17-BK-4_TN-2_TR2-TL0_S1 | 4-BK-4_TN-2_TR2-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1527 | PCU04.INV17-BK-4_TN-2_TR3-TL0_S0 | 4-BK-4_TN-2_TR3-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1528 | PCU04.INV17-BK-4_TN-2_TR3-TL0_S1 | 4-BK-4_TN-2_TR3-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1529 | PCU04.INV17-BK-4_TN-2_TR4-TL0_S0 | 4-BK-4_TN-2_TR4-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1530 | PCU04.INV17-BK-4_TN-2_TR4-TL0_S1 | 4-BK-4_TN-2_TR4-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1531 | PCU04.INV17-BK-4_TN-2_TR5-TL0_S0 | 4-BK-4_TN-2_TR5-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1532 | PCU04.INV17-BK-4_TN-2_TR5-TL0_S1 | 4-BK-4_TN-2_TR5-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1533 | PCU04.INV17-BK-4_TN-2_TR6-TL0_S0 | 4-BK-4_TN-2_TR6-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1534 | PCU04.INV17-BK-4_TN-2_TR6-TL0_S1 | 4-BK-4_TN-2_TR6-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1535 | PCU04.INV17-BK-4_TN-2_TR7-TL0_S0 | 4-BK-4_TN-2_TR7-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1536 | PCU04.INV17-BK-4_TN-2_TR7-TL0_S1 | 4-BK-4_TN-2_TR7-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1537 | PCU04.INV17-BK-4_TN-2_TR8-TL0_S0 | 4-BK-4_TN-2_TR8-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1538 | PCU04.INV17-BK-4_TN-2_TR8-TL0_S1 | 4-BK-4_TN-2_TR8-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1539 | PCU04.INV17-BK-4_TN-2_TR9-TL0_S0 | 4-BK-4_TN-2_TR9-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1540 | PCU04.INV17-BK-4_TN-2_TR9-TL0_S1 | 4-BK-4_TN-2_TR9-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1541 | PCU04.INV17-BK-4_TN-2_TR10-TL0_S0 | 4-BK-4_TN-2_TR10-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1542 | PCU04.INV17-BK-4_TN-2_TR10-TL0_S1 | 4-BK-4_TN-2_TR10-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1543 | PCU04.INV18-BK-4_TN-2_TR11-TL0_S0 | 4-BK-4_TN-2_TR11-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1544 | PCU04.INV18-BK-4_TN-2_TR11-TL0_S1 | 4-BK-4_TN-2_TR11-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1545 | PCU04.INV18-BK-4_TN-2_TR12-TL0_S0 | 4-BK-4_TN-2_TR12-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1546 | PCU04.INV18-BK-4_TN-2_TR12-TL0_S1 | 4-BK-4_TN-2_TR12-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1547 | PCU04.INV18-BK-4_TN-2_TR13-TL0_S0 | 4-BK-4_TN-2_TR13-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1548 | PCU04.INV18-BK-4_TN-2_TR13-TL0_S1 | 4-BK-4_TN-2_TR13-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1549 | PCU04.INV18-BK-4_TN-2_TR14-TL0_S0 | 4-BK-4_TN-2_TR14-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1550 | PCU04.INV18-BK-4_TN-2_TR14-TL0_S1 | 4-BK-4_TN-2_TR14-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1551 | PCU04.INV18-BK-4_TN-2_TR15-TL0_S0 | 4-BK-4_TN-2_TR15-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1552 | PCU04.INV18-BK-4_TN-2_TR15-TL0_S1 | 4-BK-4_TN-2_TR15-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1553 | PCU04.INV18-BK-4_TN-2_TR16-TL0_S0 | 4-BK-4_TN-2_TR16-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1554 | PCU04.INV18-BK-4_TN-2_TR16-TL0_S1 | 4-BK-4_TN-2_TR16-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1555 | PCU04.INV18-BK-4_TN-2_TR17-TL0_S0 | 4-BK-4_TN-2_TR17-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1556 | PCU04.INV18-BK-4_TN-2_TR17-TL0_S1 | 4-BK-4_TN-2_TR17-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1557 | PCU04.INV18-BK-4_TN-2_TR18-TL0_S0 | 4-BK-4_TN-2_TR18-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1558 | PCU04.INV18-BK-4_TN-2_TR18-TL0_S1 | 4-BK-4_TN-2_TR18-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1559 | PCU04.INV18-BK-4_TN-2_TR19-TL0_S0 | 4-BK-4_TN-2_TR19-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1560 | PCU04.INV18-BK-4_TN-2_TR19-TL0_S1 | 4-BK-4_TN-2_TR19-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1561 | PCU04.INV18-BK-4_TN-2_TR20-TL0_S0 | 4-BK-4_TN-2_TR20-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1562 | PCU04.INV18-BK-4_TN-2_TR20-TL0_S1 | 4-BK-4_TN-2_TR20-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1563 | PCU04.INV18-BK-4_TN-2_TR21-TL0_S0 | 4-BK-4_TN-2_TR21-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1564 | PCU04.INV18-BK-4_TN-2_TR21-TL0_S1 | 4-BK-4_TN-2_TR21-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1565 | PCU04.INV19-BK-4_TN-2_TR22-TL0_S0 | 4-BK-4_TN-2_TR22-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1566 | PCU04.INV19-BK-4_TN-2_TR22-TL0_S1 | 4-BK-4_TN-2_TR22-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1567 | PCU04.INV19-BK-4_TN-2_TR23-TL0_S0 | 4-BK-4_TN-2_TR23-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1568 | PCU04.INV19-BK-4_TN-2_TR23-TL0_S1 | 4-BK-4_TN-2_TR23-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1569 | PCU04.INV19-BK-4_TN-2_TR24-TL0_S0 | 4-BK-4_TN-2_TR24-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1570 | PCU04.INV19-BK-4_TN-2_TR24-TL0_S1 | 4-BK-4_TN-2_TR24-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1571 | PCU04.INV19-BK-4_TN-2_TR25-TL0_S0 | 4-BK-4_TN-2_TR25-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1572 | PCU04.INV19-BK-4_TN-2_TR25-TL0_S1 | 4-BK-4_TN-2_TR25-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1573 | PCU04.INV19-BK-4_TN-2_TR26-TL0_S0 | 4-BK-4_TN-2_TR26-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1574 | PCU04.INV19-BK-4_TN-2_TR26-TL0_S1 | 4-BK-4_TN-2_TR26-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1575 | PCU04.INV19-BK-4_TN-2_TR27-TL0_S0 | 4-BK-4_TN-2_TR27-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1576 | PCU04.INV19-BK-4_TN-2_TR27-TL0_S1 | 4-BK-4_TN-2_TR27-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1577 | PCU04.INV19-BK-4_TN-2_TR28-TL0_S0 | 4-BK-4_TN-2_TR28-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1578 | PCU04.INV19-BK-4_TN-2_TR28-TL0_S1 | 4-BK-4_TN-2_TR28-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1579 | PCU04.INV19-BK-4_TN-2_TR29-TL0_S0 | 4-BK-4_TN-2_TR29-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1580 | PCU04.INV19-BK-4_TN-2_TR29-TL0_S1 | 4-BK-4_TN-2_TR29-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1581 | PCU04.INV19-BK-4_TN-2_TR30-TL0_S0 | 4-BK-4_TN-2_TR30-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1582 | PCU04.INV19-BK-4_TN-2_TR30-TL0_S1 | 4-BK-4_TN-2_TR30-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1583 | PCU04.INV19-BK-4_TN-2_TR31-TL0_S0 | 4-BK-4_TN-2_TR31-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1584 | PCU04.INV19-BK-4_TN-2_TR31-TL0_S1 | 4-BK-4_TN-2_TR31-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1585 | PCU04.INV19-BK-4_TN-2_TR32-TL0_S0 | 4-BK-4_TN-2_TR32-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1586 | PCU04.INV19-BK-4_TN-2_TR32-TL0_S1 | 4-BK-4_TN-2_TR32-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1587 | PCU04.INV20-BK-4_TN-3_TR0-TL0_S0 | 4-BK-4_TN-3_TR0-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1588 | PCU04.INV20-BK-4_TN-3_TR0-TL0_S1 | 4-BK-4_TN-3_TR0-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1589 | PCU04.INV20-BK-4_TN-3_TR1-TL0_S0 | 4-BK-4_TN-3_TR1-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1590 | PCU04.INV20-BK-4_TN-3_TR1-TL0_S1 | 4-BK-4_TN-3_TR1-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1591 | PCU04.INV20-BK-4_TN-3_TR2-TL0_S0 | 4-BK-4_TN-3_TR2-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1592 | PCU04.INV20-BK-4_TN-3_TR2-TL0_S1 | 4-BK-4_TN-3_TR2-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1593 | PCU04.INV20-BK-4_TN-3_TR3-TL0_S0 | 4-BK-4_TN-3_TR3-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1594 | PCU04.INV20-BK-4_TN-3_TR3-TL0_S1 | 4-BK-4_TN-3_TR3-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1595 | PCU04.INV20-BK-4_TN-3_TR4-TL0_S0 | 4-BK-4_TN-3_TR4-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1596 | PCU04.INV20-BK-4_TN-3_TR4-TL0_S1 | 4-BK-4_TN-3_TR4-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1597 | PCU04.INV20-BK-4_TN-3_TR5-TL0_S0 | 4-BK-4_TN-3_TR5-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1598 | PCU04.INV20-BK-4_TN-3_TR5-TL0_S1 | 4-BK-4_TN-3_TR5-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1599 | PCU04.INV20-BK-4_TN-3_TR6-TL0_S0 | 4-BK-4_TN-3_TR6-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1600 | PCU04.INV20-BK-4_TN-3_TR6-TL0_S1 | 4-BK-4_TN-3_TR6-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 4 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1601 | PCU05.INV1-BK-5_TS-0_TR5-TL0_S0 | 5-BK-5_TS-0_TR5-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1602 | PCU05.INV1-BK-5_TS-0_TR5-TL0_S1 | 5-BK-5_TS-0_TR5-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1603 | PCU05.INV1-BK-5_TS-0_TR6-TL0_S0 | 5-BK-5_TS-0_TR6-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1604 | PCU05.INV1-BK-5_TS-0_TR6-TL0_S1 | 5-BK-5_TS-0_TR6-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1605 | PCU05.INV1-BK-5_TS-0_TR7-TL0_S0 | 5-BK-5_TS-0_TR7-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1606 | PCU05.INV1-BK-5_TS-0_TR7-TL0_S1 | 5-BK-5_TS-0_TR7-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1607 | PCU05.INV1-BK-5_TS-0_TR8-TL0_S0 | 5-BK-5_TS-0_TR8-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1608 | PCU05.INV1-BK-5_TS-0_TR8-TL0_S1 | 5-BK-5_TS-0_TR8-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1609 | PCU05.INV1-BK-5_TS-0_TR9-TL0_S0 | 5-BK-5_TS-0_TR9-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1610 | PCU05.INV1-BK-5_TS-0_TR9-TL0_S1 | 5-BK-5_TS-0_TR9-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1611 | PCU05.INV1-BK-5_TS-0_TR10-TL0_S0 | 5-BK-5_TS-0_TR10-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1612 | PCU05.INV1-BK-5_TS-0_TR10-TL0_S1 | 5-BK-5_TS-0_TR10-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1613 | PCU05.INV1-BK-5_TS-0_TR11-TL0_S0 | 5-BK-5_TS-0_TR11-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1614 | PCU05.INV1-BK-5_TS-0_TR11-TL0_S1 | 5-BK-5_TS-0_TR11-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1615 | PCU05.INV1-BK-5_TS-0_TR12-TL0_S0 | 5-BK-5_TS-0_TR12-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1616 | PCU05.INV1-BK-5_TS-0_TR12-TL0_S1 | 5-BK-5_TS-0_TR12-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1617 | PCU05.INV1-BK-5_TS-0_TR13-TL0_S0 | 5-BK-5_TS-0_TR13-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1618 | PCU05.INV1-BK-5_TS-0_TR13-TL0_S1 | 5-BK-5_TS-0_TR13-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1619 | PCU05.INV1-BK-5_TS-0_TR14-TL0_S0 | 5-BK-5_TS-0_TR14-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1620 | PCU05.INV1-BK-5_TS-0_TR14-TL0_S1 | 5-BK-5_TS-0_TR14-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1621 | PCU05.INV1-BK-5_TS-0_TR15-TL0_S0 | 5-BK-5_TS-0_TR15-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1622 | PCU05.INV1-BK-5_TS-0_TR15-TL0_S1 | 5-BK-5_TS-0_TR15-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1623 | PCU05.INV1-BK-5_TS-0_TR16-TL0_S0 | 5-BK-5_TS-0_TR16-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1624 | PCU05.INV1-BK-5_TS-0_TR16-TL0_S1 | 5-BK-5_TS-0_TR16-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1625 | PCU05.INV2-BK-5_TS-0_TR17-TL0_S0 | 5-BK-5_TS-0_TR17-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1626 | PCU05.INV2-BK-5_TS-0_TR17-TL0_S1 | 5-BK-5_TS-0_TR17-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1627 | PCU05.INV2-BK-5_TS-0_TR18-TL0_S0 | 5-BK-5_TS-0_TR18-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1628 | PCU05.INV2-BK-5_TS-0_TR18-TL0_S1 | 5-BK-5_TS-0_TR18-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1629 | PCU05.INV2-BK-5_TS-0_TR19-TL0_S0 | 5-BK-5_TS-0_TR19-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1630 | PCU05.INV2-BK-5_TS-0_TR19-TL0_S1 | 5-BK-5_TS-0_TR19-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1631 | PCU05.INV2-BK-5_TS-0_TR20-TL0_S0 | 5-BK-5_TS-0_TR20-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1632 | PCU05.INV2-BK-5_TS-0_TR20-TL0_S1 | 5-BK-5_TS-0_TR20-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1633 | PCU05.INV2-BK-5_TS-0_TR21-TL0_S0 | 5-BK-5_TS-0_TR21-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1634 | PCU05.INV2-BK-5_TS-0_TR21-TL0_S1 | 5-BK-5_TS-0_TR21-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1635 | PCU05.INV2-BK-5_TS-0_TR22-TL0_S0 | 5-BK-5_TS-0_TR22-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1636 | PCU05.INV2-BK-5_TS-0_TR22-TL0_S1 | 5-BK-5_TS-0_TR22-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1637 | PCU05.INV2-BK-5_TS-0_TR23-TL0_S0 | 5-BK-5_TS-0_TR23-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1638 | PCU05.INV2-BK-5_TS-0_TR23-TL0_S1 | 5-BK-5_TS-0_TR23-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1639 | PCU05.INV2-BK-5_TS-0_TR24-TL0_S0 | 5-BK-5_TS-0_TR24-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1640 | PCU05.INV2-BK-5_TS-0_TR24-TL0_S1 | 5-BK-5_TS-0_TR24-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1641 | PCU05.INV2-BK-5_TS-0_TR25-TL0_S0 | 5-BK-5_TS-0_TR25-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1642 | PCU05.INV2-BK-5_TS-0_TR25-TL0_S1 | 5-BK-5_TS-0_TR25-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1643 | PCU05.INV2-BK-5_TS-0_TR26-TL0_S0 | 5-BK-5_TS-0_TR26-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1644 | PCU05.INV2-BK-5_TS-0_TR26-TL0_S1 | 5-BK-5_TS-0_TR26-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1645 | PCU05.INV2-BK-5_TS-0_TR27-TL0_S0 | 5-BK-5_TS-0_TR27-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1646 | PCU05.INV2-BK-5_TS-0_TR27-TL0_S1 | 5-BK-5_TS-0_TR27-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1647 | PCU05.INV2-BK-5_TS-0_TR28-TL0_S0 | 5-BK-5_TS-0_TR28-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1648 | PCU05.INV2-BK-5_TS-0_TR28-TL0_S1 | 5-BK-5_TS-0_TR28-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1649 | PCU05.INV3-BK-5_TS-0_TR29-TL0_S0 | 5-BK-5_TS-0_TR29-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1650 | PCU05.INV3-BK-5_TS-0_TR29-TL0_S1 | 5-BK-5_TS-0_TR29-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1651 | PCU05.INV3-BK-5_TS-0_TR30-TL0_S0 | 5-BK-5_TS-0_TR30-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1652 | PCU05.INV3-BK-5_TS-0_TR30-TL0_S1 | 5-BK-5_TS-0_TR30-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1653 | PCU05.INV3-BK-5_TS-0_TR31-TL0_S0 | 5-BK-5_TS-0_TR31-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1654 | PCU05.INV3-BK-5_TS-0_TR31-TL0_S1 | 5-BK-5_TS-0_TR31-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1655 | PCU05.INV3-BK-5_TS-0_TR32-TL0_S0 | 5-BK-5_TS-0_TR32-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1656 | PCU05.INV3-BK-5_TS-0_TR32-TL0_S1 | 5-BK-5_TS-0_TR32-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1657 | PCU05.INV3-BK-5_TS-0_TR33-TL0_S0 | 5-BK-5_TS-0_TR33-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1658 | PCU05.INV3-BK-5_TS-0_TR33-TL0_S1 | 5-BK-5_TS-0_TR33-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1659 | PCU05.INV3-BK-5_TS-0_TR34-TL0_S0 | 5-BK-5_TS-0_TR34-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1660 | PCU05.INV3-BK-5_TS-0_TR34-TL0_S1 | 5-BK-5_TS-0_TR34-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1661 | PCU05.INV3-BK-5_TS-0_TR35-TL0_S0 | 5-BK-5_TS-0_TR35-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1662 | PCU05.INV3-BK-5_TS-0_TR35-TL0_S1 | 5-BK-5_TS-0_TR35-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1663 | PCU05.INV3-BK-5_TS-0_TR36-TL0_S0 | 5-BK-5_TS-0_TR36-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1664 | PCU05.INV3-BK-5_TS-0_TR36-TL0_S1 | 5-BK-5_TS-0_TR36-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1665 | PCU05.INV3-BK-5_TS-0_TR37-TL0_S0 | 5-BK-5_TS-0_TR37-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1666 | PCU05.INV3-BK-5_TS-0_TR37-TL0_S1 | 5-BK-5_TS-0_TR37-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1667 | PCU05.INV3-BK-5_TS-0_TR38-TL0_S0 | 5-BK-5_TS-0_TR38-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1668 | PCU05.INV3-BK-5_TS-0_TR38-TL0_S1 | 5-BK-5_TS-0_TR38-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1669 | PCU05.INV3-BK-5_TS-0_TR39-TL0_S0 | 5-BK-5_TS-0_TR39-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1670 | PCU05.INV3-BK-5_TS-0_TR39-TL0_S1 | 5-BK-5_TS-0_TR39-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1671 | PCU05.INV3-BK-5_TS-0_TR40-TL0_S0 | 5-BK-5_TS-0_TR40-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1672 | PCU05.INV3-BK-5_TS-0_TR40-TL0_S1 | 5-BK-5_TS-0_TR40-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1673 | PCU05.INV4-BK-5_TS-0_TR0-TL0_S0 | 5-BK-5_TS-0_TR0-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 120.2 | 60.1 | 60.1 | 21.28 | 1061.2 | 17.31 | 0 | 8.99 | 8.99 | 0.85 | 155.68 | 0.85
1674 | PCU05.INV4-BK-5_TS-0_TR0-TL0_S1 | 5-BK-5_TS-0_TR0-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 195.03 | 97.51 | 97.51 | 21.28 | 1061.2 | 17.31 | 0 | 14.59 | 14.59 | 1.38 | 252.6 | 1.38
1675 | PCU05.INV4-BK-5_TS-0_TR1-TL0_S0 | 5-BK-5_TS-0_TR1-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 110.1 | 55.05 | 55.05 | 16.28 | 1061.2 | 17.31 | 0 | 8.24 | 8.24 | 0.78 | 142.6 | 0.78
1676 | PCU05.INV4-BK-5_TS-0_TR1-TL0_S1 | 5-BK-5_TS-0_TR1-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 184.93 | 92.46 | 92.46 | 16.28 | 1061.2 | 17.31 | 0 | 13.84 | 13.84 | 1.3 | 239.52 | 1.31
1677 | PCU05.INV4-BK-5_TS-0_TR2-TL0_S0 | 5-BK-5_TS-0_TR2-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 100 | 50 | 50 | 11.28 | 1061.2 | 17.31 | 0 | 7.48 | 7.48 | 0.71 | 129.52 | 0.71
1678 | PCU05.INV4-BK-5_TS-0_TR2-TL0_S1 | 5-BK-5_TS-0_TR2-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 174.83 | 87.41 | 87.41 | 11.28 | 1061.2 | 17.31 | 0 | 13.08 | 13.08 | 1.23 | 226.44 | 1.23
1679 | PCU05.INV4-BK-5_TS-0_TR3-TL0_S0 | 5-BK-5_TS-0_TR3-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 89.9 | 44.95 | 44.95 | 6.28 | 1061.2 | 17.31 | 0 | 6.73 | 6.73 | 0.63 | 116.43 | 0.63
1680 | PCU05.INV4-BK-5_TS-0_TR3-TL0_S1 | 5-BK-5_TS-0_TR3-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 164.73 | 82.36 | 82.36 | 6.28 | 1061.2 | 17.31 | 0 | 12.33 | 12.33 | 1.16 | 213.35 | 1.16
1681 | PCU05.INV4-BK-5_TS-0_TR4-TL0_S0 | 5-BK-5_TS-0_TR4-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 100 | 50 | 50 | 11.28 | 1061.2 | 17.31 | 0 | 7.48 | 7.48 | 0.71 | 129.52 | 0.71
1682 | PCU05.INV4-BK-5_TS-0_TR4-TL0_S1 | 5-BK-5_TS-0_TR4-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 174.83 | 87.41 | 87.41 | 11.28 | 1061.2 | 17.31 | 0 | 13.08 | 13.08 | 1.23 | 226.44 | 1.23
1683 | PCU05.INV4-BK-5_TS-1_TR0-TL0_S0 | 5-BK-5_TS-1_TR0-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1684 | PCU05.INV4-BK-5_TS-1_TR0-TL0_S1 | 5-BK-5_TS-1_TR0-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1685 | PCU05.INV4-BK-5_TS-1_TR1-TL0_S0 | 5-BK-5_TS-1_TR1-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1686 | PCU05.INV4-BK-5_TS-1_TR1-TL0_S1 | 5-BK-5_TS-1_TR1-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1687 | PCU05.INV4-BK-5_TS-1_TR2-TL0_S0 | 5-BK-5_TS-1_TR2-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1688 | PCU05.INV4-BK-5_TS-1_TR2-TL0_S1 | 5-BK-5_TS-1_TR2-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1689 | PCU05.INV4-BK-5_TS-1_TR3-TL0_S0 | 5-BK-5_TS-1_TR3-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1690 | PCU05.INV4-BK-5_TS-1_TR3-TL0_S1 | 5-BK-5_TS-1_TR3-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1691 | PCU05.INV4-BK-5_TS-1_TR4-TL0_S0 | 5-BK-5_TS-1_TR4-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1692 | PCU05.INV4-BK-5_TS-1_TR4-TL0_S1 | 5-BK-5_TS-1_TR4-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1693 | PCU05.INV4-BK-5_TS-1_TR5-TL0_S0 | 5-BK-5_TS-1_TR5-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1694 | PCU05.INV4-BK-5_TS-1_TR5-TL0_S1 | 5-BK-5_TS-1_TR5-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1695 | PCU05.INV4-BK-5_TS-1_TR6-TL0_S0 | 5-BK-5_TS-1_TR6-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1696 | PCU05.INV4-BK-5_TS-1_TR6-TL0_S1 | 5-BK-5_TS-1_TR6-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1697 | PCU05.INV5-BK-5_TN-0_TR0-TL0_S0 | 5-BK-5_TN-0_TR0-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1698 | PCU05.INV5-BK-5_TN-0_TR0-TL0_S1 | 5-BK-5_TN-0_TR0-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1699 | PCU05.INV5-BK-5_TN-0_TR1-TL0_S0 | 5-BK-5_TN-0_TR1-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1700 | PCU05.INV5-BK-5_TN-0_TR1-TL0_S1 | 5-BK-5_TN-0_TR1-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1701 | PCU05.INV5-BK-5_TN-0_TR2-TL0_S0 | 5-BK-5_TN-0_TR2-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1702 | PCU05.INV5-BK-5_TN-0_TR2-TL0_S1 | 5-BK-5_TN-0_TR2-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1703 | PCU05.INV5-BK-5_TN-0_TR3-TL0_S0 | 5-BK-5_TN-0_TR3-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1704 | PCU05.INV5-BK-5_TN-0_TR3-TL0_S1 | 5-BK-5_TN-0_TR3-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1705 | PCU05.INV5-BK-5_TN-0_TR4-TL0_S0 | 5-BK-5_TN-0_TR4-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1706 | PCU05.INV5-BK-5_TN-0_TR4-TL0_S1 | 5-BK-5_TN-0_TR4-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1707 | PCU05.INV5-BK-5_TN-0_TR5-TL0_S0 | 5-BK-5_TN-0_TR5-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1708 | PCU05.INV5-BK-5_TN-0_TR5-TL0_S1 | 5-BK-5_TN-0_TR5-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1709 | PCU05.INV5-BK-5_TN-0_TR6-TL0_S0 | 5-BK-5_TN-0_TR6-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1710 | PCU05.INV5-BK-5_TN-0_TR6-TL0_S1 | 5-BK-5_TN-0_TR6-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1711 | PCU05.INV5-BK-5_TN-0_TR7-TL0_S0 | 5-BK-5_TN-0_TR7-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1712 | PCU05.INV5-BK-5_TN-0_TR7-TL0_S1 | 5-BK-5_TN-0_TR7-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1713 | PCU05.INV5-BK-5_TN-0_TR8-TL0_S0 | 5-BK-5_TN-0_TR8-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1714 | PCU05.INV5-BK-5_TN-0_TR8-TL0_S1 | 5-BK-5_TN-0_TR8-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1715 | PCU05.INV5-BK-5_TN-0_TR9-TL0_S0 | 5-BK-5_TN-0_TR9-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1716 | PCU05.INV5-BK-5_TN-0_TR9-TL0_S1 | 5-BK-5_TN-0_TR9-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1717 | PCU05.INV5-BK-5_TN-0_TR10-TL0_S0 | 5-BK-5_TN-0_TR10-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1718 | PCU05.INV5-BK-5_TN-0_TR10-TL0_S1 | 5-BK-5_TN-0_TR10-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1719 | PCU05.INV5-BK-5_TN-0_TR11-TL0_S0 | 5-BK-5_TN-0_TR11-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1720 | PCU05.INV6-BK-5_TN-0_TR11-TL0_S1 | 5-BK-5_TN-0_TR11-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1721 | PCU05.INV6-BK-5_TN-0_TR12-TL0_S0 | 5-BK-5_TN-0_TR12-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1722 | PCU05.INV6-BK-5_TN-0_TR12-TL0_S1 | 5-BK-5_TN-0_TR12-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1723 | PCU05.INV6-BK-5_TN-0_TR13-TL0_S0 | 5-BK-5_TN-0_TR13-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1724 | PCU05.INV6-BK-5_TN-0_TR13-TL0_S1 | 5-BK-5_TN-0_TR13-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1725 | PCU05.INV6-BK-5_TN-0_TR14-TL0_S0 | 5-BK-5_TN-0_TR14-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1726 | PCU05.INV6-BK-5_TN-0_TR14-TL0_S1 | 5-BK-5_TN-0_TR14-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1727 | PCU05.INV6-BK-5_TN-0_TR15-TL0_S0 | 5-BK-5_TN-0_TR15-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1728 | PCU05.INV6-BK-5_TN-0_TR15-TL0_S1 | 5-BK-5_TN-0_TR15-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1729 | PCU05.INV6-BK-5_TN-0_TR16-TL0_S0 | 5-BK-5_TN-0_TR16-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1730 | PCU05.INV6-BK-5_TN-0_TR16-TL0_S1 | 5-BK-5_TN-0_TR16-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1731 | PCU05.INV6-BK-5_TN-0_TR17-TL0_S0 | 5-BK-5_TN-0_TR17-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1732 | PCU05.INV6-BK-5_TN-0_TR17-TL0_S1 | 5-BK-5_TN-0_TR17-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1733 | PCU05.INV6-BK-5_TN-0_TR18-TL0_S0 | 5-BK-5_TN-0_TR18-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1734 | PCU05.INV6-BK-5_TN-0_TR18-TL0_S1 | 5-BK-5_TN-0_TR18-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1735 | PCU05.INV6-BK-5_TN-0_TR19-TL0_S0 | 5-BK-5_TN-0_TR19-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1736 | PCU05.INV6-BK-5_TN-0_TR19-TL0_S1 | 5-BK-5_TN-0_TR19-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1737 | PCU05.INV6-BK-5_TN-0_TR20-TL0_S0 | 5-BK-5_TN-0_TR20-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1738 | PCU05.INV6-BK-5_TN-0_TR20-TL0_S1 | 5-BK-5_TN-0_TR20-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1739 | PCU05.INV6-BK-5_TN-0_TR21-TL0_S0 | 5-BK-5_TN-0_TR21-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1740 | PCU05.INV6-BK-5_TN-0_TR21-TL0_S1 | 5-BK-5_TN-0_TR21-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1741 | PCU05.INV6-BK-5_TN-0_TR22-TL0_S0 | 5-BK-5_TN-0_TR22-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1742 | PCU05.INV7-BK-5_TN-0_TR22-TL0_S1 | 5-BK-5_TN-0_TR22-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1743 | PCU05.INV7-BK-5_TN-0_TR23-TL0_S0 | 5-BK-5_TN-0_TR23-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1744 | PCU05.INV7-BK-5_TN-0_TR23-TL0_S1 | 5-BK-5_TN-0_TR23-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1745 | PCU05.INV7-BK-5_TN-0_TR24-TL0_S0 | 5-BK-5_TN-0_TR24-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1746 | PCU05.INV7-BK-5_TN-0_TR24-TL0_S1 | 5-BK-5_TN-0_TR24-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1747 | PCU05.INV7-BK-5_TN-0_TR25-TL0_S0 | 5-BK-5_TN-0_TR25-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1748 | PCU05.INV7-BK-5_TN-0_TR25-TL0_S1 | 5-BK-5_TN-0_TR25-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1749 | PCU05.INV7-BK-5_TN-0_TR26-TL0_S0 | 5-BK-5_TN-0_TR26-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1750 | PCU05.INV7-BK-5_TN-0_TR26-TL0_S1 | 5-BK-5_TN-0_TR26-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1751 | PCU05.INV7-BK-5_TN-0_TR27-TL0_S0 | 5-BK-5_TN-0_TR27-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1752 | PCU05.INV7-BK-5_TN-0_TR27-TL0_S1 | 5-BK-5_TN-0_TR27-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1753 | PCU05.INV7-BK-5_TN-0_TR28-TL0_S0 | 5-BK-5_TN-0_TR28-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1754 | PCU05.INV7-BK-5_TN-0_TR28-TL0_S1 | 5-BK-5_TN-0_TR28-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1755 | PCU05.INV7-BK-5_TN-0_TR29-TL0_S0 | 5-BK-5_TN-0_TR29-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1756 | PCU05.INV7-BK-5_TN-0_TR29-TL0_S1 | 5-BK-5_TN-0_TR29-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1757 | PCU05.INV7-BK-5_TN-0_TR30-TL0_S0 | 5-BK-5_TN-0_TR30-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1758 | PCU05.INV7-BK-5_TN-0_TR30-TL0_S1 | 5-BK-5_TN-0_TR30-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1759 | PCU05.INV7-BK-5_TN-0_TR31-TL0_S0 | 5-BK-5_TN-0_TR31-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1760 | PCU05.INV7-BK-5_TN-0_TR31-TL0_S1 | 5-BK-5_TN-0_TR31-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1761 | PCU05.INV7-BK-5_TN-0_TR32-TL0_S0 | 5-BK-5_TN-0_TR32-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1762 | PCU05.INV7-BK-5_TN-0_TR32-TL0_S1 | 5-BK-5_TN-0_TR32-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1763 | PCU05.INV7-BK-5_TN-0_TR33-TL0_S0 | 5-BK-5_TN-0_TR33-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1764 | PCU05.INV8-BK-5_TN-0_TR33-TL0_S1 | 5-BK-5_TN-0_TR33-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1765 | PCU05.INV8-BK-5_TN-0_TR34-TL0_S0 | 5-BK-5_TN-0_TR34-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1766 | PCU05.INV8-BK-5_TN-0_TR34-TL0_S1 | 5-BK-5_TN-0_TR34-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1767 | PCU05.INV8-BK-5_TN-0_TR35-TL0_S0 | 5-BK-5_TN-0_TR35-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1768 | PCU05.INV8-BK-5_TN-0_TR35-TL0_S1 | 5-BK-5_TN-0_TR35-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1769 | PCU05.INV8-BK-5_TN-0_TR36-TL0_S0 | 5-BK-5_TN-0_TR36-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1770 | PCU05.INV8-BK-5_TN-0_TR36-TL0_S1 | 5-BK-5_TN-0_TR36-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1771 | PCU05.INV8-BK-5_TN-0_TR37-TL0_S0 | 5-BK-5_TN-0_TR37-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1772 | PCU05.INV8-BK-5_TN-0_TR37-TL0_S1 | 5-BK-5_TN-0_TR37-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1773 | PCU05.INV8-BK-5_TN-0_TR38-TL0_S0 | 5-BK-5_TN-0_TR38-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1774 | PCU05.INV8-BK-5_TN-0_TR38-TL0_S1 | 5-BK-5_TN-0_TR38-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1775 | PCU05.INV8-BK-5_TN-0_TR39-TL0_S0 | 5-BK-5_TN-0_TR39-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1776 | PCU05.INV8-BK-5_TN-0_TR39-TL0_S1 | 5-BK-5_TN-0_TR39-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1777 | PCU05.INV8-BK-5_TN-0_TR40-TL0_S0 | 5-BK-5_TN-0_TR40-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1778 | PCU05.INV8-BK-5_TN-0_TR40-TL0_S1 | 5-BK-5_TN-0_TR40-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1779 | PCU05.INV8-BK-5_TN-0_TR41-TL0_S0 | 5-BK-5_TN-0_TR41-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1780 | PCU05.INV8-BK-5_TN-0_TR41-TL0_S1 | 5-BK-5_TN-0_TR41-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1781 | PCU05.INV8-BK-5_TN-0_TR42-TL0_S0 | 5-BK-5_TN-0_TR42-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1782 | PCU05.INV8-BK-5_TN-0_TR42-TL0_S1 | 5-BK-5_TN-0_TR42-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1783 | PCU05.INV8-BK-5_TN-0_TR43-TL0_S0 | 5-BK-5_TN-0_TR43-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1784 | PCU05.INV8-BK-5_TN-0_TR43-TL0_S1 | 5-BK-5_TN-0_TR43-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1785 | PCU05.INV8-BK-5_TN-0_TR44-TL0_S0 | 5-BK-5_TN-0_TR44-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1786 | PCU05.INV8-BK-5_TN-0_TR44-TL0_S1 | 5-BK-5_TN-0_TR44-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1787 | PCU05.INV9-BK-5_TN-1_TR0-TL0_S0 | 5-BK-5_TN-1_TR0-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1788 | PCU05.INV9-BK-5_TN-1_TR0-TL0_S1 | 5-BK-5_TN-1_TR0-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1789 | PCU05.INV9-BK-5_TN-1_TR1-TL0_S0 | 5-BK-5_TN-1_TR1-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1790 | PCU05.INV9-BK-5_TN-1_TR1-TL0_S1 | 5-BK-5_TN-1_TR1-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1791 | PCU05.INV9-BK-5_TN-1_TR2-TL0_S0 | 5-BK-5_TN-1_TR2-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1792 | PCU05.INV9-BK-5_TN-1_TR2-TL0_S1 | 5-BK-5_TN-1_TR2-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1793 | PCU05.INV9-BK-5_TN-1_TR3-TL0_S0 | 5-BK-5_TN-1_TR3-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1794 | PCU05.INV9-BK-5_TN-1_TR3-TL0_S1 | 5-BK-5_TN-1_TR3-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1795 | PCU05.INV9-BK-5_TN-1_TR4-TL0_S0 | 5-BK-5_TN-1_TR4-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1796 | PCU05.INV9-BK-5_TN-1_TR4-TL0_S1 | 5-BK-5_TN-1_TR4-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1797 | PCU05.INV9-BK-5_TN-1_TR5-TL0_S0 | 5-BK-5_TN-1_TR5-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1798 | PCU05.INV9-BK-5_TN-1_TR5-TL0_S1 | 5-BK-5_TN-1_TR5-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1799 | PCU05.INV9-BK-5_TN-1_TR6-TL0_S0 | 5-BK-5_TN-1_TR6-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1800 | PCU05.INV9-BK-5_TN-1_TR6-TL0_S1 | 5-BK-5_TN-1_TR6-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1801 | PCU05.INV9-BK-5_TN-1_TR7-TL0_S0 | 5-BK-5_TN-1_TR7-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1802 | PCU05.INV9-BK-5_TN-1_TR7-TL0_S1 | 5-BK-5_TN-1_TR7-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1803 | PCU05.INV9-BK-5_TN-1_TR8-TL0_S0 | 5-BK-5_TN-1_TR8-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1804 | PCU05.INV9-BK-5_TN-1_TR8-TL0_S1 | 5-BK-5_TN-1_TR8-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1805 | PCU05.INV9-BK-5_TN-1_TR9-TL0_S0 | 5-BK-5_TN-1_TR9-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1806 | PCU05.INV9-BK-5_TN-1_TR9-TL0_S1 | 5-BK-5_TN-1_TR9-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1807 | PCU05.INV9-BK-5_TN-1_TR10-TL0_S0 | 5-BK-5_TN-1_TR10-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1808 | PCU05.INV9-BK-5_TN-1_TR10-TL0_S1 | 5-BK-5_TN-1_TR10-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1809 | PCU05.INV9-BK-5_TN-1_TR11-TL0_S0 | 5-BK-5_TN-1_TR11-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1810 | PCU05.INV10-BK-5_TN-1_TR11-TL0_S1 | 5-BK-5_TN-1_TR11-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1811 | PCU05.INV10-BK-5_TN-1_TR12-TL0_S0 | 5-BK-5_TN-1_TR12-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1812 | PCU05.INV10-BK-5_TN-1_TR12-TL0_S1 | 5-BK-5_TN-1_TR12-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1813 | PCU05.INV10-BK-5_TN-1_TR13-TL0_S0 | 5-BK-5_TN-1_TR13-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1814 | PCU05.INV10-BK-5_TN-1_TR13-TL0_S1 | 5-BK-5_TN-1_TR13-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1815 | PCU05.INV10-BK-5_TN-1_TR14-TL0_S0 | 5-BK-5_TN-1_TR14-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1816 | PCU05.INV10-BK-5_TN-1_TR14-TL0_S1 | 5-BK-5_TN-1_TR14-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1817 | PCU05.INV10-BK-5_TN-1_TR15-TL0_S0 | 5-BK-5_TN-1_TR15-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1818 | PCU05.INV10-BK-5_TN-1_TR15-TL0_S1 | 5-BK-5_TN-1_TR15-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1819 | PCU05.INV10-BK-5_TN-1_TR16-TL0_S0 | 5-BK-5_TN-1_TR16-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1820 | PCU05.INV10-BK-5_TN-1_TR16-TL0_S1 | 5-BK-5_TN-1_TR16-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1821 | PCU05.INV10-BK-5_TN-1_TR17-TL0_S0 | 5-BK-5_TN-1_TR17-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1822 | PCU05.INV10-BK-5_TN-1_TR17-TL0_S1 | 5-BK-5_TN-1_TR17-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1823 | PCU05.INV10-BK-5_TN-1_TR18-TL0_S0 | 5-BK-5_TN-1_TR18-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1824 | PCU05.INV10-BK-5_TN-1_TR18-TL0_S1 | 5-BK-5_TN-1_TR18-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1825 | PCU05.INV10-BK-5_TN-1_TR19-TL0_S0 | 5-BK-5_TN-1_TR19-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1826 | PCU05.INV10-BK-5_TN-1_TR19-TL0_S1 | 5-BK-5_TN-1_TR19-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1827 | PCU05.INV10-BK-5_TN-1_TR20-TL0_S0 | 5-BK-5_TN-1_TR20-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1828 | PCU05.INV10-BK-5_TN-1_TR20-TL0_S1 | 5-BK-5_TN-1_TR20-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1829 | PCU05.INV10-BK-5_TN-1_TR21-TL0_S0 | 5-BK-5_TN-1_TR21-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1830 | PCU05.INV10-BK-5_TN-1_TR21-TL0_S1 | 5-BK-5_TN-1_TR21-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1831 | PCU05.INV10-BK-5_TN-1_TR22-TL0_S0 | 5-BK-5_TN-1_TR22-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1832 | PCU05.INV11-BK-5_TN-1_TR22-TL0_S1 | 5-BK-5_TN-1_TR22-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1833 | PCU05.INV11-BK-5_TN-1_TR23-TL0_S0 | 5-BK-5_TN-1_TR23-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1834 | PCU05.INV11-BK-5_TN-1_TR23-TL0_S1 | 5-BK-5_TN-1_TR23-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1835 | PCU05.INV11-BK-5_TN-1_TR24-TL0_S0 | 5-BK-5_TN-1_TR24-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1836 | PCU05.INV11-BK-5_TN-1_TR24-TL0_S1 | 5-BK-5_TN-1_TR24-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1837 | PCU05.INV11-BK-5_TN-1_TR25-TL0_S0 | 5-BK-5_TN-1_TR25-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1838 | PCU05.INV11-BK-5_TN-1_TR25-TL0_S1 | 5-BK-5_TN-1_TR25-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1839 | PCU05.INV11-BK-5_TN-1_TR26-TL0_S0 | 5-BK-5_TN-1_TR26-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1840 | PCU05.INV11-BK-5_TN-1_TR26-TL0_S1 | 5-BK-5_TN-1_TR26-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1841 | PCU05.INV11-BK-5_TN-1_TR27-TL0_S0 | 5-BK-5_TN-1_TR27-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1842 | PCU05.INV11-BK-5_TN-1_TR27-TL0_S1 | 5-BK-5_TN-1_TR27-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1843 | PCU05.INV11-BK-5_TN-1_TR28-TL0_S0 | 5-BK-5_TN-1_TR28-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1844 | PCU05.INV11-BK-5_TN-1_TR28-TL0_S1 | 5-BK-5_TN-1_TR28-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1845 | PCU05.INV11-BK-5_TN-1_TR29-TL0_S0 | 5-BK-5_TN-1_TR29-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1846 | PCU05.INV11-BK-5_TN-1_TR29-TL0_S1 | 5-BK-5_TN-1_TR29-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1847 | PCU05.INV11-BK-5_TN-1_TR30-TL0_S0 | 5-BK-5_TN-1_TR30-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1848 | PCU05.INV11-BK-5_TN-1_TR30-TL0_S1 | 5-BK-5_TN-1_TR30-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1849 | PCU05.INV11-BK-5_TN-1_TR31-TL0_S0 | 5-BK-5_TN-1_TR31-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1850 | PCU05.INV11-BK-5_TN-1_TR31-TL0_S1 | 5-BK-5_TN-1_TR31-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1851 | PCU05.INV11-BK-5_TN-1_TR32-TL0_S0 | 5-BK-5_TN-1_TR32-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1852 | PCU05.INV11-BK-5_TN-1_TR32-TL0_S1 | 5-BK-5_TN-1_TR32-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1853 | PCU05.INV11-BK-5_TN-1_TR33-TL0_S0 | 5-BK-5_TN-1_TR33-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1854 | PCU05.INV12-BK-5_TN-1_TR33-TL0_S1 | 5-BK-5_TN-1_TR33-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1855 | PCU05.INV12-BK-5_TN-1_TR34-TL0_S0 | 5-BK-5_TN-1_TR34-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1856 | PCU05.INV12-BK-5_TN-1_TR34-TL0_S1 | 5-BK-5_TN-1_TR34-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1857 | PCU05.INV12-BK-5_TN-1_TR35-TL0_S0 | 5-BK-5_TN-1_TR35-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1858 | PCU05.INV12-BK-5_TN-1_TR35-TL0_S1 | 5-BK-5_TN-1_TR35-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1859 | PCU05.INV12-BK-5_TN-1_TR36-TL0_S0 | 5-BK-5_TN-1_TR36-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1860 | PCU05.INV12-BK-5_TN-1_TR36-TL0_S1 | 5-BK-5_TN-1_TR36-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1861 | PCU05.INV12-BK-5_TN-1_TR37-TL0_S0 | 5-BK-5_TN-1_TR37-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1862 | PCU05.INV12-BK-5_TN-1_TR37-TL0_S1 | 5-BK-5_TN-1_TR37-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1863 | PCU05.INV12-BK-5_TN-1_TR38-TL0_S0 | 5-BK-5_TN-1_TR38-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1864 | PCU05.INV12-BK-5_TN-1_TR38-TL0_S1 | 5-BK-5_TN-1_TR38-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1865 | PCU05.INV12-BK-5_TN-1_TR39-TL0_S0 | 5-BK-5_TN-1_TR39-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1866 | PCU05.INV12-BK-5_TN-1_TR39-TL0_S1 | 5-BK-5_TN-1_TR39-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1867 | PCU05.INV12-BK-5_TN-1_TR40-TL0_S0 | 5-BK-5_TN-1_TR40-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1868 | PCU05.INV12-BK-5_TN-1_TR40-TL0_S1 | 5-BK-5_TN-1_TR40-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1869 | PCU05.INV12-BK-5_TN-1_TR41-TL0_S0 | 5-BK-5_TN-1_TR41-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1870 | PCU05.INV12-BK-5_TN-1_TR41-TL0_S1 | 5-BK-5_TN-1_TR41-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1871 | PCU05.INV12-BK-5_TN-1_TR42-TL0_S0 | 5-BK-5_TN-1_TR42-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1872 | PCU05.INV12-BK-5_TN-1_TR42-TL0_S1 | 5-BK-5_TN-1_TR42-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1873 | PCU05.INV12-BK-5_TN-1_TR43-TL0_S0 | 5-BK-5_TN-1_TR43-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1874 | PCU05.INV12-BK-5_TN-1_TR43-TL0_S1 | 5-BK-5_TN-1_TR43-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1875 | PCU05.INV12-BK-5_TN-1_TR44-TL0_S0 | 5-BK-5_TN-1_TR44-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1876 | PCU05.INV12-BK-5_TN-1_TR44-TL0_S1 | 5-BK-5_TN-1_TR44-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1877 | PCU05.INV13-BK-5_TN-2_TR0-TL0_S0 | 5-BK-5_TN-2_TR0-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1878 | PCU05.INV13-BK-5_TN-2_TR0-TL0_S1 | 5-BK-5_TN-2_TR0-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1879 | PCU05.INV13-BK-5_TN-2_TR1-TL0_S0 | 5-BK-5_TN-2_TR1-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1880 | PCU05.INV13-BK-5_TN-2_TR1-TL0_S1 | 5-BK-5_TN-2_TR1-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1881 | PCU05.INV13-BK-5_TN-2_TR2-TL0_S0 | 5-BK-5_TN-2_TR2-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1882 | PCU05.INV13-BK-5_TN-2_TR2-TL0_S1 | 5-BK-5_TN-2_TR2-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1883 | PCU05.INV13-BK-5_TN-2_TR3-TL0_S0 | 5-BK-5_TN-2_TR3-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1884 | PCU05.INV13-BK-5_TN-2_TR3-TL0_S1 | 5-BK-5_TN-2_TR3-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1885 | PCU05.INV13-BK-5_TN-2_TR4-TL0_S0 | 5-BK-5_TN-2_TR4-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1886 | PCU05.INV13-BK-5_TN-2_TR4-TL0_S1 | 5-BK-5_TN-2_TR4-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1887 | PCU05.INV13-BK-5_TN-2_TR5-TL0_S0 | 5-BK-5_TN-2_TR5-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1888 | PCU05.INV13-BK-5_TN-2_TR5-TL0_S1 | 5-BK-5_TN-2_TR5-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1889 | PCU05.INV13-BK-5_TN-2_TR6-TL0_S0 | 5-BK-5_TN-2_TR6-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1890 | PCU05.INV13-BK-5_TN-2_TR6-TL0_S1 | 5-BK-5_TN-2_TR6-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1891 | PCU05.INV13-BK-5_TN-2_TR7-TL0_S0 | 5-BK-5_TN-2_TR7-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1892 | PCU05.INV13-BK-5_TN-2_TR7-TL0_S1 | 5-BK-5_TN-2_TR7-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1893 | PCU05.INV13-BK-5_TN-2_TR8-TL0_S0 | 5-BK-5_TN-2_TR8-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1894 | PCU05.INV13-BK-5_TN-2_TR8-TL0_S1 | 5-BK-5_TN-2_TR8-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1895 | PCU05.INV13-BK-5_TN-2_TR9-TL0_S0 | 5-BK-5_TN-2_TR9-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1896 | PCU05.INV13-BK-5_TN-2_TR9-TL0_S1 | 5-BK-5_TN-2_TR9-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1897 | PCU05.INV13-BK-5_TN-2_TR10-TL0_S0 | 5-BK-5_TN-2_TR10-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1898 | PCU05.INV13-BK-5_TN-2_TR10-TL0_S1 | 5-BK-5_TN-2_TR10-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1899 | PCU05.INV13-BK-5_TN-2_TR11-TL0_S0 | 5-BK-5_TN-2_TR11-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1900 | PCU05.INV14-BK-5_TN-2_TR11-TL0_S1 | 5-BK-5_TN-2_TR11-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1901 | PCU05.INV14-BK-5_TN-2_TR12-TL0_S0 | 5-BK-5_TN-2_TR12-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1902 | PCU05.INV14-BK-5_TN-2_TR12-TL0_S1 | 5-BK-5_TN-2_TR12-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1903 | PCU05.INV14-BK-5_TN-2_TR13-TL0_S0 | 5-BK-5_TN-2_TR13-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1904 | PCU05.INV14-BK-5_TN-2_TR13-TL0_S1 | 5-BK-5_TN-2_TR13-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1905 | PCU05.INV14-BK-5_TN-2_TR14-TL0_S0 | 5-BK-5_TN-2_TR14-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1906 | PCU05.INV14-BK-5_TN-2_TR14-TL0_S1 | 5-BK-5_TN-2_TR14-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1907 | PCU05.INV14-BK-5_TN-2_TR15-TL0_S0 | 5-BK-5_TN-2_TR15-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1908 | PCU05.INV14-BK-5_TN-2_TR15-TL0_S1 | 5-BK-5_TN-2_TR15-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1909 | PCU05.INV14-BK-5_TN-2_TR16-TL0_S0 | 5-BK-5_TN-2_TR16-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1910 | PCU05.INV14-BK-5_TN-2_TR16-TL0_S1 | 5-BK-5_TN-2_TR16-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1911 | PCU05.INV14-BK-5_TN-2_TR17-TL0_S0 | 5-BK-5_TN-2_TR17-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1912 | PCU05.INV14-BK-5_TN-2_TR17-TL0_S1 | 5-BK-5_TN-2_TR17-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1913 | PCU05.INV14-BK-5_TN-2_TR18-TL0_S0 | 5-BK-5_TN-2_TR18-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1914 | PCU05.INV14-BK-5_TN-2_TR18-TL0_S1 | 5-BK-5_TN-2_TR18-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1915 | PCU05.INV14-BK-5_TN-2_TR19-TL0_S0 | 5-BK-5_TN-2_TR19-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1916 | PCU05.INV14-BK-5_TN-2_TR19-TL0_S1 | 5-BK-5_TN-2_TR19-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1917 | PCU05.INV14-BK-5_TN-2_TR20-TL0_S0 | 5-BK-5_TN-2_TR20-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1918 | PCU05.INV14-BK-5_TN-2_TR20-TL0_S1 | 5-BK-5_TN-2_TR20-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1919 | PCU05.INV14-BK-5_TN-2_TR21-TL0_S0 | 5-BK-5_TN-2_TR21-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1920 | PCU05.INV14-BK-5_TN-2_TR21-TL0_S1 | 5-BK-5_TN-2_TR21-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1921 | PCU05.INV14-BK-5_TN-2_TR22-TL0_S0 | 5-BK-5_TN-2_TR22-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1922 | PCU05.INV15-BK-5_TN-2_TR22-TL0_S1 | 5-BK-5_TN-2_TR22-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1923 | PCU05.INV15-BK-5_TN-2_TR23-TL0_S0 | 5-BK-5_TN-2_TR23-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1924 | PCU05.INV15-BK-5_TN-2_TR23-TL0_S1 | 5-BK-5_TN-2_TR23-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1925 | PCU05.INV15-BK-5_TN-2_TR24-TL0_S0 | 5-BK-5_TN-2_TR24-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1926 | PCU05.INV15-BK-5_TN-2_TR24-TL0_S1 | 5-BK-5_TN-2_TR24-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1927 | PCU05.INV15-BK-5_TN-2_TR25-TL0_S0 | 5-BK-5_TN-2_TR25-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1928 | PCU05.INV15-BK-5_TN-2_TR25-TL0_S1 | 5-BK-5_TN-2_TR25-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1929 | PCU05.INV15-BK-5_TN-2_TR26-TL0_S0 | 5-BK-5_TN-2_TR26-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1930 | PCU05.INV15-BK-5_TN-2_TR26-TL0_S1 | 5-BK-5_TN-2_TR26-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1931 | PCU05.INV15-BK-5_TN-2_TR27-TL0_S0 | 5-BK-5_TN-2_TR27-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1932 | PCU05.INV15-BK-5_TN-2_TR27-TL0_S1 | 5-BK-5_TN-2_TR27-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1933 | PCU05.INV15-BK-5_TN-2_TR28-TL0_S0 | 5-BK-5_TN-2_TR28-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1934 | PCU05.INV15-BK-5_TN-2_TR28-TL0_S1 | 5-BK-5_TN-2_TR28-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1935 | PCU05.INV15-BK-5_TN-2_TR29-TL0_S0 | 5-BK-5_TN-2_TR29-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1936 | PCU05.INV15-BK-5_TN-2_TR29-TL0_S1 | 5-BK-5_TN-2_TR29-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1937 | PCU05.INV15-BK-5_TN-2_TR30-TL0_S0 | 5-BK-5_TN-2_TR30-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1938 | PCU05.INV15-BK-5_TN-2_TR30-TL0_S1 | 5-BK-5_TN-2_TR30-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1939 | PCU05.INV15-BK-5_TN-2_TR31-TL0_S0 | 5-BK-5_TN-2_TR31-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1940 | PCU05.INV15-BK-5_TN-2_TR31-TL0_S1 | 5-BK-5_TN-2_TR31-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1941 | PCU05.INV15-BK-5_TN-2_TR32-TL0_S0 | 5-BK-5_TN-2_TR32-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1942 | PCU05.INV15-BK-5_TN-2_TR32-TL0_S1 | 5-BK-5_TN-2_TR32-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1943 | PCU05.INV15-BK-5_TN-2_TR33-TL0_S0 | 5-BK-5_TN-2_TR33-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1944 | PCU05.INV16-BK-5_TN-2_TR33-TL0_S1 | 5-BK-5_TN-2_TR33-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1945 | PCU05.INV16-BK-5_TN-2_TR34-TL0_S0 | 5-BK-5_TN-2_TR34-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1946 | PCU05.INV16-BK-5_TN-2_TR34-TL0_S1 | 5-BK-5_TN-2_TR34-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1947 | PCU05.INV16-BK-5_TN-2_TR35-TL0_S0 | 5-BK-5_TN-2_TR35-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1948 | PCU05.INV16-BK-5_TN-2_TR35-TL0_S1 | 5-BK-5_TN-2_TR35-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1949 | PCU05.INV16-BK-5_TN-2_TR36-TL0_S0 | 5-BK-5_TN-2_TR36-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1950 | PCU05.INV16-BK-5_TN-2_TR36-TL0_S1 | 5-BK-5_TN-2_TR36-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1951 | PCU05.INV16-BK-5_TN-2_TR37-TL0_S0 | 5-BK-5_TN-2_TR37-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1952 | PCU05.INV16-BK-5_TN-2_TR37-TL0_S1 | 5-BK-5_TN-2_TR37-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1953 | PCU05.INV16-BK-5_TN-2_TR38-TL0_S0 | 5-BK-5_TN-2_TR38-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1954 | PCU05.INV16-BK-5_TN-2_TR38-TL0_S1 | 5-BK-5_TN-2_TR38-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1955 | PCU05.INV16-BK-5_TN-2_TR39-TL0_S0 | 5-BK-5_TN-2_TR39-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1956 | PCU05.INV16-BK-5_TN-2_TR39-TL0_S1 | 5-BK-5_TN-2_TR39-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1957 | PCU05.INV16-BK-5_TN-2_TR40-TL0_S0 | 5-BK-5_TN-2_TR40-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1958 | PCU05.INV16-BK-5_TN-2_TR40-TL0_S1 | 5-BK-5_TN-2_TR40-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1959 | PCU05.INV16-BK-5_TN-2_TR41-TL0_S0 | 5-BK-5_TN-2_TR41-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1960 | PCU05.INV16-BK-5_TN-2_TR41-TL0_S1 | 5-BK-5_TN-2_TR41-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1961 | PCU05.INV16-BK-5_TN-2_TR42-TL0_S0 | 5-BK-5_TN-2_TR42-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1962 | PCU05.INV16-BK-5_TN-2_TR42-TL0_S1 | 5-BK-5_TN-2_TR42-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1963 | PCU05.INV16-BK-5_TN-2_TR43-TL0_S0 | 5-BK-5_TN-2_TR43-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1964 | PCU05.INV16-BK-5_TN-2_TR43-TL0_S1 | 5-BK-5_TN-2_TR43-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1965 | PCU05.INV16-BK-5_TN-2_TR44-TL0_S0 | 5-BK-5_TN-2_TR44-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1966 | PCU05.INV16-BK-5_TN-2_TR44-TL0_S1 | 5-BK-5_TN-2_TR44-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1967 | PCU05.INV17-BK-5_TN-3_TR0-TL0_S0 | 5-BK-5_TN-3_TR0-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
1968 | PCU05.INV17-BK-5_TN-3_TR0-TL0_S1 | 5-BK-5_TN-3_TR0-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1969 | PCU05.INV17-BK-5_TN-3_TR1-TL0_S0 | 5-BK-5_TN-3_TR1-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1970 | PCU05.INV17-BK-5_TN-3_TR1-TL0_S1 | 5-BK-5_TN-3_TR1-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1971 | PCU05.INV17-BK-5_TN-3_TR2-TL0_S0 | 5-BK-5_TN-3_TR2-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1972 | PCU05.INV17-BK-5_TN-3_TR2-TL0_S1 | 5-BK-5_TN-3_TR2-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1973 | PCU05.INV17-BK-5_TN-3_TR3-TL0_S0 | 5-BK-5_TN-3_TR3-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1974 | PCU05.INV17-BK-5_TN-3_TR3-TL0_S1 | 5-BK-5_TN-3_TR3-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1975 | PCU05.INV17-BK-5_TN-3_TR4-TL0_S0 | 5-BK-5_TN-3_TR4-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1976 | PCU05.INV17-BK-5_TN-3_TR4-TL0_S1 | 5-BK-5_TN-3_TR4-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1977 | PCU05.INV17-BK-5_TN-3_TR5-TL0_S0 | 5-BK-5_TN-3_TR5-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1978 | PCU05.INV17-BK-5_TN-3_TR5-TL0_S1 | 5-BK-5_TN-3_TR5-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1979 | PCU05.INV17-BK-5_TN-3_TR6-TL0_S0 | 5-BK-5_TN-3_TR6-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
1980 | PCU05.INV17-BK-5_TN-3_TR6-TL0_S1 | 5-BK-5_TN-3_TR6-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
1981 | PCU05.INV17-BK-5_TN-3_TR7-TL0_S0 | 5-BK-5_TN-3_TR7-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
1982 | PCU05.INV17-BK-5_TN-3_TR7-TL0_S1 | 5-BK-5_TN-3_TR7-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
1983 | PCU05.INV17-BK-5_TN-3_TR8-TL0_S0 | 5-BK-5_TN-3_TR8-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1984 | PCU05.INV17-BK-5_TN-3_TR8-TL0_S1 | 5-BK-5_TN-3_TR8-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1985 | PCU05.INV17-BK-5_TN-3_TR9-TL0_S0 | 5-BK-5_TN-3_TR9-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1986 | PCU05.INV17-BK-5_TN-3_TR9-TL0_S1 | 5-BK-5_TN-3_TR9-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1987 | PCU05.INV17-BK-5_TN-3_TR10-TL0_S0 | 5-BK-5_TN-3_TR10-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1988 | PCU05.INV17-BK-5_TN-3_TR10-TL0_S1 | 5-BK-5_TN-3_TR10-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1989 | PCU05.INV17-BK-5_TN-3_TR11-TL0_S0 | 5-BK-5_TN-3_TR11-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1990 | PCU05.INV18-BK-5_TN-3_TR11-TL0_S1 | 5-BK-5_TN-3_TR11-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
1991 | PCU05.INV18-BK-5_TN-3_TR12-TL0_S0 | 5-BK-5_TN-3_TR12-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
1992 | PCU05.INV18-BK-5_TN-3_TR12-TL0_S1 | 5-BK-5_TN-3_TR12-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
1993 | PCU05.INV18-BK-5_TN-3_TR13-TL0_S0 | 5-BK-5_TN-3_TR13-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
1994 | PCU05.INV18-BK-5_TN-3_TR13-TL0_S1 | 5-BK-5_TN-3_TR13-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
1995 | PCU05.INV18-BK-5_TN-3_TR14-TL0_S0 | 5-BK-5_TN-3_TR14-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
1996 | PCU05.INV18-BK-5_TN-3_TR14-TL0_S1 | 5-BK-5_TN-3_TR14-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
1997 | PCU05.INV18-BK-5_TN-3_TR15-TL0_S0 | 5-BK-5_TN-3_TR15-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
1998 | PCU05.INV18-BK-5_TN-3_TR15-TL0_S1 | 5-BK-5_TN-3_TR15-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
1999 | PCU05.INV18-BK-5_TN-3_TR16-TL0_S0 | 5-BK-5_TN-3_TR16-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2000 | PCU05.INV18-BK-5_TN-3_TR16-TL0_S1 | 5-BK-5_TN-3_TR16-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2001 | PCU05.INV18-BK-5_TN-3_TR17-TL0_S0 | 5-BK-5_TN-3_TR17-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2002 | PCU05.INV18-BK-5_TN-3_TR17-TL0_S1 | 5-BK-5_TN-3_TR17-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2003 | PCU05.INV18-BK-5_TN-3_TR18-TL0_S0 | 5-BK-5_TN-3_TR18-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2004 | PCU05.INV18-BK-5_TN-3_TR18-TL0_S1 | 5-BK-5_TN-3_TR18-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2005 | PCU05.INV18-BK-5_TN-3_TR19-TL0_S0 | 5-BK-5_TN-3_TR19-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2006 | PCU05.INV18-BK-5_TN-3_TR19-TL0_S1 | 5-BK-5_TN-3_TR19-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2007 | PCU05.INV18-BK-5_TN-3_TR20-TL0_S0 | 5-BK-5_TN-3_TR20-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2008 | PCU05.INV18-BK-5_TN-3_TR20-TL0_S1 | 5-BK-5_TN-3_TR20-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2009 | PCU05.INV18-BK-5_TN-3_TR21-TL0_S0 | 5-BK-5_TN-3_TR21-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2010 | PCU05.INV18-BK-5_TN-3_TR21-TL0_S1 | 5-BK-5_TN-3_TR21-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2011 | PCU05.INV18-BK-5_TN-3_TR22-TL0_S0 | 5-BK-5_TN-3_TR22-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2012 | PCU05.INV19-BK-5_TN-3_TR22-TL0_S1 | 5-BK-5_TN-3_TR22-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2013 | PCU05.INV19-BK-5_TN-3_TR23-TL0_S0 | 5-BK-5_TN-3_TR23-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2014 | PCU05.INV19-BK-5_TN-3_TR23-TL0_S1 | 5-BK-5_TN-3_TR23-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2015 | PCU05.INV19-BK-5_TN-3_TR24-TL0_S0 | 5-BK-5_TN-3_TR24-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2016 | PCU05.INV19-BK-5_TN-3_TR24-TL0_S1 | 5-BK-5_TN-3_TR24-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2017 | PCU05.INV19-BK-5_TN-3_TR25-TL0_S0 | 5-BK-5_TN-3_TR25-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2018 | PCU05.INV19-BK-5_TN-3_TR25-TL0_S1 | 5-BK-5_TN-3_TR25-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2019 | PCU05.INV19-BK-5_TN-3_TR26-TL0_S0 | 5-BK-5_TN-3_TR26-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2020 | PCU05.INV19-BK-5_TN-3_TR26-TL0_S1 | 5-BK-5_TN-3_TR26-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2021 | PCU05.INV19-BK-5_TN-3_TR27-TL0_S0 | 5-BK-5_TN-3_TR27-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2022 | PCU05.INV19-BK-5_TN-3_TR27-TL0_S1 | 5-BK-5_TN-3_TR27-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2023 | PCU05.INV19-BK-5_TN-3_TR28-TL0_S0 | 5-BK-5_TN-3_TR28-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2024 | PCU05.INV19-BK-5_TN-3_TR28-TL0_S1 | 5-BK-5_TN-3_TR28-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2025 | PCU05.INV19-BK-5_TN-3_TR29-TL0_S0 | 5-BK-5_TN-3_TR29-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2026 | PCU05.INV19-BK-5_TN-3_TR29-TL0_S1 | 5-BK-5_TN-3_TR29-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2027 | PCU05.INV19-BK-5_TN-3_TR30-TL0_S0 | 5-BK-5_TN-3_TR30-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2028 | PCU05.INV19-BK-5_TN-3_TR30-TL0_S1 | 5-BK-5_TN-3_TR30-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2029 | PCU05.INV19-BK-5_TN-3_TR31-TL0_S0 | 5-BK-5_TN-3_TR31-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2030 | PCU05.INV19-BK-5_TN-3_TR31-TL0_S1 | 5-BK-5_TN-3_TR31-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2031 | PCU05.INV19-BK-5_TN-3_TR32-TL0_S0 | 5-BK-5_TN-3_TR32-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2032 | PCU05.INV19-BK-5_TN-3_TR32-TL0_S1 | 5-BK-5_TN-3_TR32-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2033 | PCU05.INV19-BK-5_TN-3_TR33-TL0_S0 | 5-BK-5_TN-3_TR33-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
2034 | PCU05.INV20-BK-5_TN-3_TR33-TL0_S1 | 5-BK-5_TN-3_TR33-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2035 | PCU05.INV20-BK-5_TN-3_TR34-TL0_S0 | 5-BK-5_TN-3_TR34-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2036 | PCU05.INV20-BK-5_TN-3_TR34-TL0_S1 | 5-BK-5_TN-3_TR34-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2037 | PCU05.INV20-BK-5_TN-3_TR35-TL0_S0 | 5-BK-5_TN-3_TR35-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2038 | PCU05.INV20-BK-5_TN-3_TR35-TL0_S1 | 5-BK-5_TN-3_TR35-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2039 | PCU05.INV20-BK-5_TN-3_TR36-TL0_S0 | 5-BK-5_TN-3_TR36-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2040 | PCU05.INV20-BK-5_TN-3_TR36-TL0_S1 | 5-BK-5_TN-3_TR36-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2041 | PCU05.INV20-BK-5_TN-3_TR37-TL0_S0 | 5-BK-5_TN-3_TR37-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2042 | PCU05.INV20-BK-5_TN-3_TR37-TL0_S1 | 5-BK-5_TN-3_TR37-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2043 | PCU05.INV20-BK-5_TN-3_TR38-TL0_S0 | 5-BK-5_TN-3_TR38-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2044 | PCU05.INV20-BK-5_TN-3_TR38-TL0_S1 | 5-BK-5_TN-3_TR38-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2045 | PCU05.INV20-BK-5_TN-3_TR39-TL0_S0 | 5-BK-5_TN-3_TR39-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2046 | PCU05.INV20-BK-5_TN-3_TR39-TL0_S1 | 5-BK-5_TN-3_TR39-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2047 | PCU05.INV20-BK-5_TN-3_TR40-TL0_S0 | 5-BK-5_TN-3_TR40-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2048 | PCU05.INV20-BK-5_TN-3_TR40-TL0_S1 | 5-BK-5_TN-3_TR40-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2049 | PCU05.INV20-BK-5_TN-3_TR41-TL0_S0 | 5-BK-5_TN-3_TR41-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2050 | PCU05.INV20-BK-5_TN-3_TR41-TL0_S1 | 5-BK-5_TN-3_TR41-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2051 | PCU05.INV20-BK-5_TN-3_TR42-TL0_S0 | 5-BK-5_TN-3_TR42-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2052 | PCU05.INV20-BK-5_TN-3_TR42-TL0_S1 | 5-BK-5_TN-3_TR42-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2053 | PCU05.INV20-BK-5_TN-3_TR43-TL0_S0 | 5-BK-5_TN-3_TR43-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2054 | PCU05.INV20-BK-5_TN-3_TR43-TL0_S1 | 5-BK-5_TN-3_TR43-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2055 | PCU05.INV20-BK-5_TN-3_TR44-TL0_S0 | 5-BK-5_TN-3_TR44-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
2056 | PCU05.INV20-BK-5_TN-3_TR44-TL0_S1 | 5-BK-5_TN-3_TR44-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 5 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
2057 | PCU06.INV1-BK-6_TS-0_TR0-TL0_S0 | 6-BK-6_TS-0_TR0-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2058 | PCU06.INV1-BK-6_TS-0_TR0-TL0_S1 | 6-BK-6_TS-0_TR0-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2059 | PCU06.INV1-BK-6_TS-0_TR1-TL0_S0 | 6-BK-6_TS-0_TR1-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2060 | PCU06.INV1-BK-6_TS-0_TR1-TL0_S1 | 6-BK-6_TS-0_TR1-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2061 | PCU06.INV1-BK-6_TS-0_TR2-TL0_S0 | 6-BK-6_TS-0_TR2-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2062 | PCU06.INV1-BK-6_TS-0_TR2-TL0_S1 | 6-BK-6_TS-0_TR2-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2063 | PCU06.INV1-BK-6_TS-0_TR3-TL0_S0 | 6-BK-6_TS-0_TR3-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2064 | PCU06.INV1-BK-6_TS-0_TR3-TL0_S1 | 6-BK-6_TS-0_TR3-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2065 | PCU06.INV1-BK-6_TS-0_TR4-TL0_S0 | 6-BK-6_TS-0_TR4-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2066 | PCU06.INV1-BK-6_TS-0_TR4-TL0_S1 | 6-BK-6_TS-0_TR4-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2067 | PCU06.INV1-BK-6_TS-0_TR5-TL0_S0 | 6-BK-6_TS-0_TR5-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2068 | PCU06.INV1-BK-6_TS-0_TR5-TL0_S1 | 6-BK-6_TS-0_TR5-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2069 | PCU06.INV1-BK-6_TS-0_TR6-TL0_S0 | 6-BK-6_TS-0_TR6-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2070 | PCU06.INV1-BK-6_TS-0_TR6-TL0_S1 | 6-BK-6_TS-0_TR6-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2071 | PCU06.INV1-BK-6_TS-0_TR7-TL0_S0 | 6-BK-6_TS-0_TR7-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2072 | PCU06.INV1-BK-6_TS-0_TR7-TL0_S1 | 6-BK-6_TS-0_TR7-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2073 | PCU06.INV1-BK-6_TS-0_TR8-TL0_S0 | 6-BK-6_TS-0_TR8-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2074 | PCU06.INV1-BK-6_TS-0_TR8-TL0_S1 | 6-BK-6_TS-0_TR8-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2075 | PCU06.INV1-BK-6_TS-0_TR9-TL0_S0 | 6-BK-6_TS-0_TR9-TL0_S0 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2076 | PCU06.INV1-BK-6_TS-0_TR9-TL0_S1 | 6-BK-6_TS-0_TR9-TL0_S1 | INV1 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2077 | PCU06.INV2-BK-6_TS-0_TR10-TL0_S0 | 6-BK-6_TS-0_TR10-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2078 | PCU06.INV2-BK-6_TS-0_TR10-TL0_S1 | 6-BK-6_TS-0_TR10-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2079 | PCU06.INV2-BK-6_TS-0_TR11-TL0_S0 | 6-BK-6_TS-0_TR11-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2080 | PCU06.INV2-BK-6_TS-0_TR11-TL0_S1 | 6-BK-6_TS-0_TR11-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2081 | PCU06.INV2-BK-6_TS-0_TR12-TL0_S0 | 6-BK-6_TS-0_TR12-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2082 | PCU06.INV2-BK-6_TS-0_TR12-TL0_S1 | 6-BK-6_TS-0_TR12-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2083 | PCU06.INV2-BK-6_TS-0_TR13-TL0_S0 | 6-BK-6_TS-0_TR13-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2084 | PCU06.INV2-BK-6_TS-0_TR13-TL0_S1 | 6-BK-6_TS-0_TR13-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2085 | PCU06.INV2-BK-6_TS-0_TR14-TL0_S0 | 6-BK-6_TS-0_TR14-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2086 | PCU06.INV2-BK-6_TS-0_TR14-TL0_S1 | 6-BK-6_TS-0_TR14-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2087 | PCU06.INV2-BK-6_TS-0_TR15-TL0_S0 | 6-BK-6_TS-0_TR15-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2088 | PCU06.INV2-BK-6_TS-0_TR15-TL0_S1 | 6-BK-6_TS-0_TR15-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2089 | PCU06.INV2-BK-6_TS-0_TR16-TL0_S0 | 6-BK-6_TS-0_TR16-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2090 | PCU06.INV2-BK-6_TS-0_TR16-TL0_S1 | 6-BK-6_TS-0_TR16-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2091 | PCU06.INV2-BK-6_TS-0_TR17-TL0_S0 | 6-BK-6_TS-0_TR17-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2092 | PCU06.INV2-BK-6_TS-0_TR17-TL0_S1 | 6-BK-6_TS-0_TR17-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2093 | PCU06.INV2-BK-6_TS-0_TR18-TL0_S0 | 6-BK-6_TS-0_TR18-TL0_S0 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2094 | PCU06.INV2-BK-6_TS-0_TR18-TL0_S1 | 6-BK-6_TS-0_TR18-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2095 | PCU06.INV2-BK-6_TS-0_TR19-TL0_S1 | 6-BK-6_TS-0_TR19-TL0_S1 | INV2 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2096 | PCU06.INV3-BK-6_TS-0_TR19-TL0_S0 | 6-BK-6_TS-0_TR19-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2097 | PCU06.INV3-BK-6_TS-0_TR20-TL0_S0 | 6-BK-6_TS-0_TR20-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2098 | PCU06.INV3-BK-6_TS-0_TR20-TL0_S1 | 6-BK-6_TS-0_TR20-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2099 | PCU06.INV3-BK-6_TS-0_TR21-TL0_S0 | 6-BK-6_TS-0_TR21-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2100 | PCU06.INV3-BK-6_TS-0_TR21-TL0_S1 | 6-BK-6_TS-0_TR21-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2101 | PCU06.INV3-BK-6_TS-0_TR22-TL0_S0 | 6-BK-6_TS-0_TR22-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2102 | PCU06.INV3-BK-6_TS-0_TR22-TL0_S1 | 6-BK-6_TS-0_TR22-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2103 | PCU06.INV3-BK-6_TS-0_TR23-TL0_S0 | 6-BK-6_TS-0_TR23-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2104 | PCU06.INV3-BK-6_TS-0_TR23-TL0_S1 | 6-BK-6_TS-0_TR23-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2105 | PCU06.INV3-BK-6_TS-0_TR24-TL0_S0 | 6-BK-6_TS-0_TR24-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2106 | PCU06.INV3-BK-6_TS-0_TR24-TL0_S1 | 6-BK-6_TS-0_TR24-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2107 | PCU06.INV3-BK-6_TS-0_TR25-TL0_S0 | 6-BK-6_TS-0_TR25-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2108 | PCU06.INV3-BK-6_TS-0_TR25-TL0_S1 | 6-BK-6_TS-0_TR25-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2109 | PCU06.INV3-BK-6_TS-0_TR26-TL0_S0 | 6-BK-6_TS-0_TR26-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2110 | PCU06.INV3-BK-6_TS-0_TR26-TL0_S1 | 6-BK-6_TS-0_TR26-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2111 | PCU06.INV3-BK-6_TS-0_TR27-TL0_S0 | 6-BK-6_TS-0_TR27-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2112 | PCU06.INV3-BK-6_TS-0_TR27-TL0_S1 | 6-BK-6_TS-0_TR27-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2113 | PCU06.INV3-BK-6_TS-0_TR28-TL0_S0 | 6-BK-6_TS-0_TR28-TL0_S0 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2114 | PCU06.INV3-BK-6_TS-0_TR28-TL0_S1 | 6-BK-6_TS-0_TR28-TL0_S1 | INV3 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2115 | PCU06.INV4-BK-6_TS-0_TR29-TL0_S0 | 6-BK-6_TS-0_TR29-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2116 | PCU06.INV4-BK-6_TS-0_TR29-TL0_S1 | 6-BK-6_TS-0_TR29-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2117 | PCU06.INV4-BK-6_TS-0_TR30-TL0_S0 | 6-BK-6_TS-0_TR30-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2118 | PCU06.INV4-BK-6_TS-0_TR30-TL0_S1 | 6-BK-6_TS-0_TR30-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2119 | PCU06.INV4-BK-6_TS-0_TR31-TL0_S0 | 6-BK-6_TS-0_TR31-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2120 | PCU06.INV4-BK-6_TS-0_TR31-TL0_S1 | 6-BK-6_TS-0_TR31-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2121 | PCU06.INV4-BK-6_TS-0_TR32-TL0_S0 | 6-BK-6_TS-0_TR32-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2122 | PCU06.INV4-BK-6_TS-0_TR32-TL0_S1 | 6-BK-6_TS-0_TR32-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2123 | PCU06.INV4-BK-6_TS-0_TR33-TL0_S0 | 6-BK-6_TS-0_TR33-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2124 | PCU06.INV4-BK-6_TS-0_TR33-TL0_S1 | 6-BK-6_TS-0_TR33-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2125 | PCU06.INV4-BK-6_TS-0_TR34-TL0_S0 | 6-BK-6_TS-0_TR34-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2126 | PCU06.INV4-BK-6_TS-0_TR34-TL0_S1 | 6-BK-6_TS-0_TR34-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2127 | PCU06.INV4-BK-6_TS-0_TR35-TL0_S0 | 6-BK-6_TS-0_TR35-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2128 | PCU06.INV4-BK-6_TS-0_TR35-TL0_S1 | 6-BK-6_TS-0_TR35-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2129 | PCU06.INV4-BK-6_TS-0_TR36-TL0_S0 | 6-BK-6_TS-0_TR36-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2130 | PCU06.INV4-BK-6_TS-0_TR36-TL0_S1 | 6-BK-6_TS-0_TR36-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2131 | PCU06.INV4-BK-6_TS-0_TR37-TL0_S0 | 6-BK-6_TS-0_TR37-TL0_S0 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2132 | PCU06.INV4-BK-6_TS-0_TR37-TL0_S1 | 6-BK-6_TS-0_TR37-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2133 | PCU06.INV4-BK-6_TS-0_TR38-TL0_S1 | 6-BK-6_TS-0_TR38-TL0_S1 | INV4 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2134 | PCU06.INV5-BK-6_TS-0_TR38-TL0_S0 | 6-BK-6_TS-0_TR38-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2135 | PCU06.INV5-BK-6_TS-0_TR39-TL0_S0 | 6-BK-6_TS-0_TR39-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2136 | PCU06.INV5-BK-6_TS-0_TR39-TL0_S1 | 6-BK-6_TS-0_TR39-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2137 | PCU06.INV5-BK-6_TS-0_TR40-TL0_S0 | 6-BK-6_TS-0_TR40-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2138 | PCU06.INV5-BK-6_TS-0_TR40-TL0_S1 | 6-BK-6_TS-0_TR40-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2139 | PCU06.INV5-BK-6_TS-0_TR41-TL0_S0 | 6-BK-6_TS-0_TR41-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2140 | PCU06.INV5-BK-6_TS-0_TR41-TL0_S1 | 6-BK-6_TS-0_TR41-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2141 | PCU06.INV5-BK-6_TS-0_TR42-TL0_S0 | 6-BK-6_TS-0_TR42-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2142 | PCU06.INV5-BK-6_TS-0_TR42-TL0_S1 | 6-BK-6_TS-0_TR42-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2143 | PCU06.INV5-BK-6_TS-0_TR43-TL0_S0 | 6-BK-6_TS-0_TR43-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2144 | PCU06.INV5-BK-6_TS-0_TR43-TL0_S1 | 6-BK-6_TS-0_TR43-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2145 | PCU06.INV5-BK-6_TS-0_TR44-TL0_S0 | 6-BK-6_TS-0_TR44-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2146 | PCU06.INV5-BK-6_TS-0_TR44-TL0_S1 | 6-BK-6_TS-0_TR44-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2147 | PCU06.INV5-BK-6_TS-0_TR45-TL0_S0 | 6-BK-6_TS-0_TR45-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2148 | PCU06.INV5-BK-6_TS-0_TR45-TL0_S1 | 6-BK-6_TS-0_TR45-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2149 | PCU06.INV5-BK-6_TS-0_TR46-TL0_S0 | 6-BK-6_TS-0_TR46-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2150 | PCU06.INV5-BK-6_TS-0_TR46-TL0_S1 | 6-BK-6_TS-0_TR46-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2151 | PCU06.INV5-BK-6_TS-0_TR47-TL0_S0 | 6-BK-6_TS-0_TR47-TL0_S0 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2152 | PCU06.INV5-BK-6_TS-0_TR47-TL0_S1 | 6-BK-6_TS-0_TR47-TL0_S1 | INV5 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2153 | PCU06.INV6-BK-6_TS-1_TR0-TL0_S0 | 6-BK-6_TS-1_TR0-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
2154 | PCU06.INV6-BK-6_TS-1_TR0-TL0_S1 | 6-BK-6_TS-1_TR0-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
2155 | PCU06.INV6-BK-6_TS-1_TR1-TL0_S0 | 6-BK-6_TS-1_TR1-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2156 | PCU06.INV6-BK-6_TS-1_TR1-TL0_S1 | 6-BK-6_TS-1_TR1-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2157 | PCU06.INV6-BK-6_TS-1_TR2-TL0_S0 | 6-BK-6_TS-1_TR2-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2158 | PCU06.INV6-BK-6_TS-1_TR2-TL0_S1 | 6-BK-6_TS-1_TR2-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2159 | PCU06.INV6-BK-6_TS-1_TR3-TL0_S0 | 6-BK-6_TS-1_TR3-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2160 | PCU06.INV6-BK-6_TS-1_TR3-TL0_S1 | 6-BK-6_TS-1_TR3-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2161 | PCU06.INV6-BK-6_TS-1_TR4-TL0_S0 | 6-BK-6_TS-1_TR4-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2162 | PCU06.INV6-BK-6_TS-1_TR4-TL0_S1 | 6-BK-6_TS-1_TR4-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2163 | PCU06.INV6-BK-6_TS-1_TR5-TL0_S0 | 6-BK-6_TS-1_TR5-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2164 | PCU06.INV6-BK-6_TS-1_TR5-TL0_S1 | 6-BK-6_TS-1_TR5-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2165 | PCU06.INV6-BK-6_TS-1_TR6-TL0_S0 | 6-BK-6_TS-1_TR6-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2166 | PCU06.INV6-BK-6_TS-1_TR6-TL0_S1 | 6-BK-6_TS-1_TR6-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2167 | PCU06.INV6-BK-6_TS-1_TR7-TL0_S0 | 6-BK-6_TS-1_TR7-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2168 | PCU06.INV6-BK-6_TS-1_TR7-TL0_S1 | 6-BK-6_TS-1_TR7-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2169 | PCU06.INV6-BK-6_TS-1_TR8-TL0_S0 | 6-BK-6_TS-1_TR8-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2170 | PCU06.INV6-BK-6_TS-1_TR8-TL0_S1 | 6-BK-6_TS-1_TR8-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2171 | PCU06.INV6-BK-6_TS-1_TR9-TL0_S0 | 6-BK-6_TS-1_TR9-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2172 | PCU06.INV6-BK-6_TS-1_TR9-TL0_S1 | 6-BK-6_TS-1_TR9-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2173 | PCU06.INV6-BK-6_TS-1_TR10-TL0_S0 | 6-BK-6_TS-1_TR10-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2174 | PCU06.INV6-BK-6_TS-1_TR10-TL0_S1 | 6-BK-6_TS-1_TR10-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2175 | PCU06.INV6-BK-6_TS-1_TR11-TL0_S0 | 6-BK-6_TS-1_TR11-TL0_S0 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2176 | PCU06.INV6-BK-6_TS-1_TR11-TL0_S1 | 6-BK-6_TS-1_TR11-TL0_S1 | INV6 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2177 | PCU06.INV7-BK-6_TS-1_TR12-TL0_S0 | 6-BK-6_TS-1_TR12-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
2178 | PCU06.INV7-BK-6_TS-1_TR12-TL0_S1 | 6-BK-6_TS-1_TR12-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
2179 | PCU06.INV7-BK-6_TS-1_TR13-TL0_S0 | 6-BK-6_TS-1_TR13-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2180 | PCU06.INV7-BK-6_TS-1_TR13-TL0_S1 | 6-BK-6_TS-1_TR13-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2181 | PCU06.INV7-BK-6_TS-1_TR14-TL0_S0 | 6-BK-6_TS-1_TR14-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2182 | PCU06.INV7-BK-6_TS-1_TR14-TL0_S1 | 6-BK-6_TS-1_TR14-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2183 | PCU06.INV7-BK-6_TS-1_TR15-TL0_S0 | 6-BK-6_TS-1_TR15-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2184 | PCU06.INV7-BK-6_TS-1_TR15-TL0_S1 | 6-BK-6_TS-1_TR15-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2185 | PCU06.INV7-BK-6_TS-1_TR16-TL0_S0 | 6-BK-6_TS-1_TR16-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2186 | PCU06.INV7-BK-6_TS-1_TR16-TL0_S1 | 6-BK-6_TS-1_TR16-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2187 | PCU06.INV7-BK-6_TS-1_TR17-TL0_S0 | 6-BK-6_TS-1_TR17-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2188 | PCU06.INV7-BK-6_TS-1_TR17-TL0_S1 | 6-BK-6_TS-1_TR17-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2189 | PCU06.INV7-BK-6_TS-1_TR18-TL0_S0 | 6-BK-6_TS-1_TR18-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2190 | PCU06.INV7-BK-6_TS-1_TR18-TL0_S1 | 6-BK-6_TS-1_TR18-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2191 | PCU06.INV7-BK-6_TS-1_TR19-TL0_S0 | 6-BK-6_TS-1_TR19-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2192 | PCU06.INV7-BK-6_TS-1_TR19-TL0_S1 | 6-BK-6_TS-1_TR19-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2193 | PCU06.INV7-BK-6_TS-1_TR20-TL0_S0 | 6-BK-6_TS-1_TR20-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2194 | PCU06.INV7-BK-6_TS-1_TR20-TL0_S1 | 6-BK-6_TS-1_TR20-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2195 | PCU06.INV7-BK-6_TS-1_TR21-TL0_S0 | 6-BK-6_TS-1_TR21-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2196 | PCU06.INV7-BK-6_TS-1_TR21-TL0_S1 | 6-BK-6_TS-1_TR21-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2197 | PCU06.INV7-BK-6_TS-1_TR22-TL0_S0 | 6-BK-6_TS-1_TR22-TL0_S0 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2198 | PCU06.INV7-BK-6_TS-1_TR22-TL0_S1 | 6-BK-6_TS-1_TR22-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2199 | PCU06.INV7-BK-6_TS-1_TR23-TL0_S1 | 6-BK-6_TS-1_TR23-TL0_S1 | INV7 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2200 | PCU06.INV8-BK-6_TS-1_TR23-TL0_S0 | 6-BK-6_TS-1_TR23-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2201 | PCU06.INV8-BK-6_TS-1_TR24-TL0_S0 | 6-BK-6_TS-1_TR24-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2202 | PCU06.INV8-BK-6_TS-1_TR24-TL0_S1 | 6-BK-6_TS-1_TR24-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2203 | PCU06.INV8-BK-6_TS-1_TR25-TL0_S0 | 6-BK-6_TS-1_TR25-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2204 | PCU06.INV8-BK-6_TS-1_TR25-TL0_S1 | 6-BK-6_TS-1_TR25-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2205 | PCU06.INV8-BK-6_TS-1_TR26-TL0_S0 | 6-BK-6_TS-1_TR26-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2206 | PCU06.INV8-BK-6_TS-1_TR26-TL0_S1 | 6-BK-6_TS-1_TR26-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2207 | PCU06.INV8-BK-6_TS-1_TR27-TL0_S0 | 6-BK-6_TS-1_TR27-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2208 | PCU06.INV8-BK-6_TS-1_TR27-TL0_S1 | 6-BK-6_TS-1_TR27-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2209 | PCU06.INV8-BK-6_TS-1_TR28-TL0_S0 | 6-BK-6_TS-1_TR28-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2210 | PCU06.INV8-BK-6_TS-1_TR28-TL0_S1 | 6-BK-6_TS-1_TR28-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2211 | PCU06.INV8-BK-6_TS-1_TR29-TL0_S0 | 6-BK-6_TS-1_TR29-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2212 | PCU06.INV8-BK-6_TS-1_TR29-TL0_S1 | 6-BK-6_TS-1_TR29-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2213 | PCU06.INV8-BK-6_TS-1_TR30-TL0_S0 | 6-BK-6_TS-1_TR30-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2214 | PCU06.INV8-BK-6_TS-1_TR30-TL0_S1 | 6-BK-6_TS-1_TR30-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2215 | PCU06.INV8-BK-6_TS-1_TR31-TL0_S0 | 6-BK-6_TS-1_TR31-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2216 | PCU06.INV8-BK-6_TS-1_TR31-TL0_S1 | 6-BK-6_TS-1_TR31-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2217 | PCU06.INV8-BK-6_TS-1_TR32-TL0_S0 | 6-BK-6_TS-1_TR32-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2218 | PCU06.INV8-BK-6_TS-1_TR32-TL0_S1 | 6-BK-6_TS-1_TR32-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2219 | PCU06.INV8-BK-6_TS-1_TR33-TL0_S0 | 6-BK-6_TS-1_TR33-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2220 | PCU06.INV8-BK-6_TS-1_TR33-TL0_S1 | 6-BK-6_TS-1_TR33-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2221 | PCU06.INV8-BK-6_TS-1_TR34-TL0_S0 | 6-BK-6_TS-1_TR34-TL0_S0 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
2222 | PCU06.INV8-BK-6_TS-1_TR34-TL0_S1 | 6-BK-6_TS-1_TR34-TL0_S1 | INV8 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
2223 | PCU06.INV9-BK-6_TS-2_TR0-TL0_S0 | 6-BK-6_TS-2_TR0-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2224 | PCU06.INV9-BK-6_TS-2_TR0-TL0_S1 | 6-BK-6_TS-2_TR0-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2225 | PCU06.INV9-BK-6_TS-2_TR1-TL0_S0 | 6-BK-6_TS-2_TR1-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2226 | PCU06.INV9-BK-6_TS-2_TR1-TL0_S1 | 6-BK-6_TS-2_TR1-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2227 | PCU06.INV9-BK-6_TS-2_TR2-TL0_S0 | 6-BK-6_TS-2_TR2-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2228 | PCU06.INV9-BK-6_TS-2_TR2-TL0_S1 | 6-BK-6_TS-2_TR2-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2229 | PCU06.INV9-BK-6_TS-2_TR3-TL0_S0 | 6-BK-6_TS-2_TR3-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2230 | PCU06.INV9-BK-6_TS-2_TR3-TL0_S1 | 6-BK-6_TS-2_TR3-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2231 | PCU06.INV9-BK-6_TS-2_TR4-TL0_S0 | 6-BK-6_TS-2_TR4-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2232 | PCU06.INV9-BK-6_TS-2_TR4-TL0_S1 | 6-BK-6_TS-2_TR4-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2233 | PCU06.INV9-BK-6_TS-2_TR5-TL0_S0 | 6-BK-6_TS-2_TR5-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2234 | PCU06.INV9-BK-6_TS-2_TR5-TL0_S1 | 6-BK-6_TS-2_TR5-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2235 | PCU06.INV9-BK-6_TS-2_TR6-TL0_S0 | 6-BK-6_TS-2_TR6-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2236 | PCU06.INV9-BK-6_TS-2_TR6-TL0_S1 | 6-BK-6_TS-2_TR6-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2237 | PCU06.INV9-BK-6_TS-2_TR7-TL0_S0 | 6-BK-6_TS-2_TR7-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2238 | PCU06.INV9-BK-6_TS-2_TR7-TL0_S1 | 6-BK-6_TS-2_TR7-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2239 | PCU06.INV9-BK-6_TS-2_TR8-TL0_S0 | 6-BK-6_TS-2_TR8-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2240 | PCU06.INV9-BK-6_TS-2_TR8-TL0_S1 | 6-BK-6_TS-2_TR8-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2241 | PCU06.INV9-BK-6_TS-2_TR9-TL0_S0 | 6-BK-6_TS-2_TR9-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2242 | PCU06.INV9-BK-6_TS-2_TR9-TL0_S1 | 6-BK-6_TS-2_TR9-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2243 | PCU06.INV9-BK-6_TS-2_TR10-TL0_S0 | 6-BK-6_TS-2_TR10-TL0_S0 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2244 | PCU06.INV9-BK-6_TS-2_TR10-TL0_S1 | 6-BK-6_TS-2_TR10-TL0_S1 | INV9 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2245 | PCU06.INV10-BK-6_TS-2_TR11-TL0_S0 | 6-BK-6_TS-2_TR11-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2246 | PCU06.INV10-BK-6_TS-2_TR11-TL0_S1 | 6-BK-6_TS-2_TR11-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2247 | PCU06.INV10-BK-6_TS-2_TR12-TL0_S0 | 6-BK-6_TS-2_TR12-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2248 | PCU06.INV10-BK-6_TS-2_TR12-TL0_S1 | 6-BK-6_TS-2_TR12-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2249 | PCU06.INV10-BK-6_TS-2_TR13-TL0_S0 | 6-BK-6_TS-2_TR13-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2250 | PCU06.INV10-BK-6_TS-2_TR13-TL0_S1 | 6-BK-6_TS-2_TR13-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2251 | PCU06.INV10-BK-6_TS-2_TR14-TL0_S0 | 6-BK-6_TS-2_TR14-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2252 | PCU06.INV10-BK-6_TS-2_TR14-TL0_S1 | 6-BK-6_TS-2_TR14-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2253 | PCU06.INV10-BK-6_TS-2_TR15-TL0_S0 | 6-BK-6_TS-2_TR15-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2254 | PCU06.INV10-BK-6_TS-2_TR15-TL0_S1 | 6-BK-6_TS-2_TR15-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2255 | PCU06.INV10-BK-6_TS-2_TR16-TL0_S0 | 6-BK-6_TS-2_TR16-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2256 | PCU06.INV10-BK-6_TS-2_TR16-TL0_S1 | 6-BK-6_TS-2_TR16-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2257 | PCU06.INV10-BK-6_TS-2_TR17-TL0_S0 | 6-BK-6_TS-2_TR17-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2258 | PCU06.INV10-BK-6_TS-2_TR17-TL0_S1 | 6-BK-6_TS-2_TR17-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2259 | PCU06.INV10-BK-6_TS-2_TR18-TL0_S0 | 6-BK-6_TS-2_TR18-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2260 | PCU06.INV10-BK-6_TS-2_TR18-TL0_S1 | 6-BK-6_TS-2_TR18-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2261 | PCU06.INV10-BK-6_TS-2_TR19-TL0_S0 | 6-BK-6_TS-2_TR19-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2262 | PCU06.INV10-BK-6_TS-2_TR19-TL0_S1 | 6-BK-6_TS-2_TR19-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2263 | PCU06.INV10-BK-6_TS-2_TR20-TL0_S0 | 6-BK-6_TS-2_TR20-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2264 | PCU06.INV10-BK-6_TS-2_TR20-TL0_S1 | 6-BK-6_TS-2_TR20-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2265 | PCU06.INV10-BK-6_TS-2_TR21-TL0_S0 | 6-BK-6_TS-2_TR21-TL0_S0 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2266 | PCU06.INV10-BK-6_TS-2_TR21-TL0_S1 | 6-BK-6_TS-2_TR21-TL0_S1 | INV10 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2267 | PCU06.INV11-BK-6_TN-0_TR0-TL0_S0 | 6-BK-6_TN-0_TR0-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
2268 | PCU06.INV11-BK-6_TN-0_TR0-TL0_S1 | 6-BK-6_TN-0_TR0-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
2269 | PCU06.INV11-BK-6_TN-0_TR1-TL0_S0 | 6-BK-6_TN-0_TR1-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2270 | PCU06.INV11-BK-6_TN-0_TR1-TL0_S1 | 6-BK-6_TN-0_TR1-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2271 | PCU06.INV11-BK-6_TN-0_TR2-TL0_S0 | 6-BK-6_TN-0_TR2-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2272 | PCU06.INV11-BK-6_TN-0_TR2-TL0_S1 | 6-BK-6_TN-0_TR2-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2273 | PCU06.INV11-BK-6_TN-0_TR3-TL0_S0 | 6-BK-6_TN-0_TR3-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2274 | PCU06.INV11-BK-6_TN-0_TR3-TL0_S1 | 6-BK-6_TN-0_TR3-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2275 | PCU06.INV11-BK-6_TN-0_TR4-TL0_S0 | 6-BK-6_TN-0_TR4-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2276 | PCU06.INV11-BK-6_TN-0_TR4-TL0_S1 | 6-BK-6_TN-0_TR4-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2277 | PCU06.INV11-BK-6_TN-0_TR5-TL0_S0 | 6-BK-6_TN-0_TR5-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2278 | PCU06.INV11-BK-6_TN-0_TR5-TL0_S1 | 6-BK-6_TN-0_TR5-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2279 | PCU06.INV11-BK-6_TN-0_TR6-TL0_S0 | 6-BK-6_TN-0_TR6-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2280 | PCU06.INV11-BK-6_TN-0_TR6-TL0_S1 | 6-BK-6_TN-0_TR6-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2281 | PCU06.INV11-BK-6_TN-0_TR7-TL0_S0 | 6-BK-6_TN-0_TR7-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2282 | PCU06.INV11-BK-6_TN-0_TR7-TL0_S1 | 6-BK-6_TN-0_TR7-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2283 | PCU06.INV11-BK-6_TN-0_TR8-TL0_S0 | 6-BK-6_TN-0_TR8-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2284 | PCU06.INV11-BK-6_TN-0_TR8-TL0_S1 | 6-BK-6_TN-0_TR8-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2285 | PCU06.INV11-BK-6_TN-0_TR9-TL0_S0 | 6-BK-6_TN-0_TR9-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2286 | PCU06.INV11-BK-6_TN-0_TR9-TL0_S1 | 6-BK-6_TN-0_TR9-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2287 | PCU06.INV11-BK-6_TN-0_TR10-TL0_S0 | 6-BK-6_TN-0_TR10-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2288 | PCU06.INV11-BK-6_TN-0_TR10-TL0_S1 | 6-BK-6_TN-0_TR10-TL0_S1 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2289 | PCU06.INV11-BK-6_TN-0_TR11-TL0_S0 | 6-BK-6_TN-0_TR11-TL0_S0 | INV11 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2290 | PCU06.INV12-BK-6_TN-0_TR11-TL0_S1 | 6-BK-6_TN-0_TR11-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
2291 | PCU06.INV12-BK-6_TN-0_TR12-TL0_S0 | 6-BK-6_TN-0_TR12-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2292 | PCU06.INV12-BK-6_TN-0_TR12-TL0_S1 | 6-BK-6_TN-0_TR12-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2293 | PCU06.INV12-BK-6_TN-0_TR13-TL0_S0 | 6-BK-6_TN-0_TR13-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2294 | PCU06.INV12-BK-6_TN-0_TR13-TL0_S1 | 6-BK-6_TN-0_TR13-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2295 | PCU06.INV12-BK-6_TN-0_TR14-TL0_S0 | 6-BK-6_TN-0_TR14-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2296 | PCU06.INV12-BK-6_TN-0_TR14-TL0_S1 | 6-BK-6_TN-0_TR14-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2297 | PCU06.INV12-BK-6_TN-0_TR15-TL0_S0 | 6-BK-6_TN-0_TR15-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2298 | PCU06.INV12-BK-6_TN-0_TR15-TL0_S1 | 6-BK-6_TN-0_TR15-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2299 | PCU06.INV12-BK-6_TN-0_TR16-TL0_S0 | 6-BK-6_TN-0_TR16-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2300 | PCU06.INV12-BK-6_TN-0_TR16-TL0_S1 | 6-BK-6_TN-0_TR16-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2301 | PCU06.INV12-BK-6_TN-0_TR17-TL0_S0 | 6-BK-6_TN-0_TR17-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2302 | PCU06.INV12-BK-6_TN-0_TR17-TL0_S1 | 6-BK-6_TN-0_TR17-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2303 | PCU06.INV12-BK-6_TN-0_TR18-TL0_S0 | 6-BK-6_TN-0_TR18-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2304 | PCU06.INV12-BK-6_TN-0_TR18-TL0_S1 | 6-BK-6_TN-0_TR18-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2305 | PCU06.INV12-BK-6_TN-0_TR19-TL0_S0 | 6-BK-6_TN-0_TR19-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2306 | PCU06.INV12-BK-6_TN-0_TR19-TL0_S1 | 6-BK-6_TN-0_TR19-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2307 | PCU06.INV12-BK-6_TN-0_TR20-TL0_S0 | 6-BK-6_TN-0_TR20-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2308 | PCU06.INV12-BK-6_TN-0_TR20-TL0_S1 | 6-BK-6_TN-0_TR20-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2309 | PCU06.INV12-BK-6_TN-0_TR21-TL0_S0 | 6-BK-6_TN-0_TR21-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2310 | PCU06.INV12-BK-6_TN-0_TR21-TL0_S1 | 6-BK-6_TN-0_TR21-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2311 | PCU06.INV12-BK-6_TN-0_TR22-TL0_S0 | 6-BK-6_TN-0_TR22-TL0_S0 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2312 | PCU06.INV12-BK-6_TN-0_TR22-TL0_S1 | 6-BK-6_TN-0_TR22-TL0_S1 | INV12 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2313 | PCU06.INV13-BK-6_TN-0_TR23-TL0_S0 | 6-BK-6_TN-0_TR23-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2314 | PCU06.INV13-BK-6_TN-0_TR23-TL0_S1 | 6-BK-6_TN-0_TR23-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2315 | PCU06.INV13-BK-6_TN-0_TR24-TL0_S0 | 6-BK-6_TN-0_TR24-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2316 | PCU06.INV13-BK-6_TN-0_TR24-TL0_S1 | 6-BK-6_TN-0_TR24-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2317 | PCU06.INV13-BK-6_TN-0_TR25-TL0_S0 | 6-BK-6_TN-0_TR25-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2318 | PCU06.INV13-BK-6_TN-0_TR25-TL0_S1 | 6-BK-6_TN-0_TR25-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2319 | PCU06.INV13-BK-6_TN-0_TR26-TL0_S0 | 6-BK-6_TN-0_TR26-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2320 | PCU06.INV13-BK-6_TN-0_TR26-TL0_S1 | 6-BK-6_TN-0_TR26-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2321 | PCU06.INV13-BK-6_TN-0_TR27-TL0_S0 | 6-BK-6_TN-0_TR27-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2322 | PCU06.INV13-BK-6_TN-0_TR27-TL0_S1 | 6-BK-6_TN-0_TR27-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2323 | PCU06.INV13-BK-6_TN-0_TR28-TL0_S0 | 6-BK-6_TN-0_TR28-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2324 | PCU06.INV13-BK-6_TN-0_TR28-TL0_S1 | 6-BK-6_TN-0_TR28-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2325 | PCU06.INV13-BK-6_TN-0_TR29-TL0_S0 | 6-BK-6_TN-0_TR29-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2326 | PCU06.INV13-BK-6_TN-0_TR29-TL0_S1 | 6-BK-6_TN-0_TR29-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2327 | PCU06.INV13-BK-6_TN-0_TR30-TL0_S0 | 6-BK-6_TN-0_TR30-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2328 | PCU06.INV13-BK-6_TN-0_TR30-TL0_S1 | 6-BK-6_TN-0_TR30-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2329 | PCU06.INV13-BK-6_TN-0_TR31-TL0_S0 | 6-BK-6_TN-0_TR31-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2330 | PCU06.INV13-BK-6_TN-0_TR31-TL0_S1 | 6-BK-6_TN-0_TR31-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2331 | PCU06.INV13-BK-6_TN-0_TR32-TL0_S0 | 6-BK-6_TN-0_TR32-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2332 | PCU06.INV13-BK-6_TN-0_TR32-TL0_S1 | 6-BK-6_TN-0_TR32-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2333 | PCU06.INV13-BK-6_TN-0_TR33-TL0_S0 | 6-BK-6_TN-0_TR33-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2334 | PCU06.INV13-BK-6_TN-0_TR33-TL0_S1 | 6-BK-6_TN-0_TR33-TL0_S1 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2335 | PCU06.INV13-BK-6_TN-0_TR34-TL0_S0 | 6-BK-6_TN-0_TR34-TL0_S0 | INV13 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
2336 | PCU06.INV14-BK-6_TN-0_TR34-TL0_S1 | 6-BK-6_TN-0_TR34-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2337 | PCU06.INV14-BK-6_TN-0_TR35-TL0_S0 | 6-BK-6_TN-0_TR35-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2338 | PCU06.INV14-BK-6_TN-0_TR35-TL0_S1 | 6-BK-6_TN-0_TR35-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2339 | PCU06.INV14-BK-6_TN-0_TR36-TL0_S0 | 6-BK-6_TN-0_TR36-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2340 | PCU06.INV14-BK-6_TN-0_TR36-TL0_S1 | 6-BK-6_TN-0_TR36-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2341 | PCU06.INV14-BK-6_TN-0_TR37-TL0_S0 | 6-BK-6_TN-0_TR37-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2342 | PCU06.INV14-BK-6_TN-0_TR37-TL0_S1 | 6-BK-6_TN-0_TR37-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2343 | PCU06.INV14-BK-6_TN-0_TR38-TL0_S0 | 6-BK-6_TN-0_TR38-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2344 | PCU06.INV14-BK-6_TN-0_TR38-TL0_S1 | 6-BK-6_TN-0_TR38-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2345 | PCU06.INV14-BK-6_TN-0_TR39-TL0_S0 | 6-BK-6_TN-0_TR39-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2346 | PCU06.INV14-BK-6_TN-0_TR39-TL0_S1 | 6-BK-6_TN-0_TR39-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2347 | PCU06.INV14-BK-6_TN-0_TR40-TL0_S0 | 6-BK-6_TN-0_TR40-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2348 | PCU06.INV14-BK-6_TN-0_TR40-TL0_S1 | 6-BK-6_TN-0_TR40-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2349 | PCU06.INV14-BK-6_TN-0_TR41-TL0_S0 | 6-BK-6_TN-0_TR41-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2350 | PCU06.INV14-BK-6_TN-0_TR41-TL0_S1 | 6-BK-6_TN-0_TR41-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2351 | PCU06.INV14-BK-6_TN-0_TR42-TL0_S0 | 6-BK-6_TN-0_TR42-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2352 | PCU06.INV14-BK-6_TN-0_TR42-TL0_S1 | 6-BK-6_TN-0_TR42-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2353 | PCU06.INV14-BK-6_TN-0_TR43-TL0_S0 | 6-BK-6_TN-0_TR43-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2354 | PCU06.INV14-BK-6_TN-0_TR43-TL0_S1 | 6-BK-6_TN-0_TR43-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2355 | PCU06.INV14-BK-6_TN-0_TR44-TL0_S0 | 6-BK-6_TN-0_TR44-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2356 | PCU06.INV14-BK-6_TN-0_TR44-TL0_S1 | 6-BK-6_TN-0_TR44-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2357 | PCU06.INV14-BK-6_TN-0_TR45-TL0_S0 | 6-BK-6_TN-0_TR45-TL0_S0 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
2358 | PCU06.INV14-BK-6_TN-0_TR45-TL0_S1 | 6-BK-6_TN-0_TR45-TL0_S1 | INV14 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
2359 | PCU06.INV15-BK-6_TN-0_TR50-TL0_S1 | 6-BK-6_TN-0_TR50-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2360 | PCU06.INV15-BK-6_TN-0_TR51-TL0_S0 | 6-BK-6_TN-0_TR51-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2361 | PCU06.INV15-BK-6_TN-0_TR51-TL0_S1 | 6-BK-6_TN-0_TR51-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2362 | PCU06.INV15-BK-6_TN-0_TR52-TL0_S0 | 6-BK-6_TN-0_TR52-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2363 | PCU06.INV15-BK-6_TN-0_TR52-TL0_S1 | 6-BK-6_TN-0_TR52-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2364 | PCU06.INV15-BK-6_TN-0_TR53-TL0_S0 | 6-BK-6_TN-0_TR53-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2365 | PCU06.INV15-BK-6_TN-0_TR53-TL0_S1 | 6-BK-6_TN-0_TR53-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2366 | PCU06.INV15-BK-6_TN-0_TR54-TL0_S0 | 6-BK-6_TN-0_TR54-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2367 | PCU06.INV15-BK-6_TN-0_TR54-TL0_S1 | 6-BK-6_TN-0_TR54-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2368 | PCU06.INV15-BK-6_TN-0_TR55-TL0_S0 | 6-BK-6_TN-0_TR55-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2369 | PCU06.INV15-BK-6_TN-0_TR55-TL0_S1 | 6-BK-6_TN-0_TR55-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2370 | PCU06.INV15-BK-6_TN-0_TR56-TL0_S0 | 6-BK-6_TN-0_TR56-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2371 | PCU06.INV15-BK-6_TN-0_TR56-TL0_S1 | 6-BK-6_TN-0_TR56-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2372 | PCU06.INV15-BK-6_TN-0_TR57-TL0_S0 | 6-BK-6_TN-0_TR57-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2373 | PCU06.INV15-BK-6_TN-0_TR57-TL0_S1 | 6-BK-6_TN-0_TR57-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2374 | PCU06.INV15-BK-6_TN-0_TR58-TL0_S0 | 6-BK-6_TN-0_TR58-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2375 | PCU06.INV15-BK-6_TN-0_TR58-TL0_S1 | 6-BK-6_TN-0_TR58-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2376 | PCU06.INV15-BK-6_TN-0_TR59-TL0_S0 | 6-BK-6_TN-0_TR59-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2377 | PCU06.INV15-BK-6_TN-0_TR59-TL0_S1 | 6-BK-6_TN-0_TR59-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2378 | PCU06.INV15-BK-6_TN-0_TR60-TL0_S0 | 6-BK-6_TN-0_TR60-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2379 | PCU06.INV15-BK-6_TN-0_TR60-TL0_S1 | 6-BK-6_TN-0_TR60-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2380 | PCU06.INV15-BK-6_TN-0_TR61-TL0_S0 | 6-BK-6_TN-0_TR61-TL0_S0 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 74.13 | 37.07 | 37.07 | 32.5 | 1061.2 | 17.31 | 0 | 5.55 | 5.55 | 0.52 | 96.02 | 0.52
2381 | PCU06.INV15-BK-6_TN-0_TR61-TL0_S1 | 6-BK-6_TN-0_TR61-TL0_S1 | INV15 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 148.96 | 74.48 | 74.48 | 32.5 | 1061.2 | 17.31 | 0 | 11.15 | 11.15 | 1.05 | 192.94 | 1.05
2382 | PCU06.INV16-BK-6_TN-1_TR0-TL0_S0 | 6-BK-6_TN-1_TR0-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2383 | PCU06.INV16-BK-6_TN-1_TR0-TL0_S1 | 6-BK-6_TN-1_TR0-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2384 | PCU06.INV16-BK-6_TN-1_TR1-TL0_S0 | 6-BK-6_TN-1_TR1-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2385 | PCU06.INV16-BK-6_TN-1_TR1-TL0_S1 | 6-BK-6_TN-1_TR1-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2386 | PCU06.INV16-BK-6_TN-1_TR2-TL0_S0 | 6-BK-6_TN-1_TR2-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2387 | PCU06.INV16-BK-6_TN-1_TR2-TL0_S1 | 6-BK-6_TN-1_TR2-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2388 | PCU06.INV16-BK-6_TN-1_TR3-TL0_S0 | 6-BK-6_TN-1_TR3-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2389 | PCU06.INV16-BK-6_TN-1_TR3-TL0_S1 | 6-BK-6_TN-1_TR3-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2390 | PCU06.INV16-BK-6_TN-1_TR4-TL0_S0 | 6-BK-6_TN-1_TR4-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2391 | PCU06.INV16-BK-6_TN-1_TR4-TL0_S1 | 6-BK-6_TN-1_TR4-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2392 | PCU06.INV16-BK-6_TN-1_TR5-TL0_S0 | 6-BK-6_TN-1_TR5-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2393 | PCU06.INV16-BK-6_TN-1_TR5-TL0_S1 | 6-BK-6_TN-1_TR5-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2394 | PCU06.INV16-BK-6_TN-1_TR6-TL0_S0 | 6-BK-6_TN-1_TR6-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2395 | PCU06.INV16-BK-6_TN-1_TR6-TL0_S1 | 6-BK-6_TN-1_TR6-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2396 | PCU06.INV16-BK-6_TN-1_TR7-TL0_S0 | 6-BK-6_TN-1_TR7-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2397 | PCU06.INV16-BK-6_TN-1_TR7-TL0_S1 | 6-BK-6_TN-1_TR7-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2398 | PCU06.INV16-BK-6_TN-1_TR8-TL0_S0 | 6-BK-6_TN-1_TR8-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2399 | PCU06.INV16-BK-6_TN-1_TR8-TL0_S1 | 6-BK-6_TN-1_TR8-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2400 | PCU06.INV16-BK-6_TN-1_TR9-TL0_S0 | 6-BK-6_TN-1_TR9-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2401 | PCU06.INV16-BK-6_TN-1_TR9-TL0_S1 | 6-BK-6_TN-1_TR9-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2402 | PCU06.INV16-BK-6_TN-1_TR10-TL0_S0 | 6-BK-6_TN-1_TR10-TL0_S0 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2403 | PCU06.INV16-BK-6_TN-1_TR10-TL0_S1 | 6-BK-6_TN-1_TR10-TL0_S1 | INV16 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2404 | PCU06.INV17-BK-6_TN-1_TR11-TL0_S0 | 6-BK-6_TN-1_TR11-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2405 | PCU06.INV17-BK-6_TN-1_TR11-TL0_S1 | 6-BK-6_TN-1_TR11-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2406 | PCU06.INV17-BK-6_TN-1_TR12-TL0_S0 | 6-BK-6_TN-1_TR12-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2407 | PCU06.INV17-BK-6_TN-1_TR12-TL0_S1 | 6-BK-6_TN-1_TR12-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2408 | PCU06.INV17-BK-6_TN-1_TR13-TL0_S0 | 6-BK-6_TN-1_TR13-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2409 | PCU06.INV17-BK-6_TN-1_TR13-TL0_S1 | 6-BK-6_TN-1_TR13-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2410 | PCU06.INV17-BK-6_TN-1_TR14-TL0_S0 | 6-BK-6_TN-1_TR14-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2411 | PCU06.INV17-BK-6_TN-1_TR14-TL0_S1 | 6-BK-6_TN-1_TR14-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2412 | PCU06.INV17-BK-6_TN-1_TR15-TL0_S0 | 6-BK-6_TN-1_TR15-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2413 | PCU06.INV17-BK-6_TN-1_TR15-TL0_S1 | 6-BK-6_TN-1_TR15-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2414 | PCU06.INV17-BK-6_TN-1_TR16-TL0_S0 | 6-BK-6_TN-1_TR16-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2415 | PCU06.INV17-BK-6_TN-1_TR16-TL0_S1 | 6-BK-6_TN-1_TR16-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2416 | PCU06.INV17-BK-6_TN-1_TR17-TL0_S0 | 6-BK-6_TN-1_TR17-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2417 | PCU06.INV17-BK-6_TN-1_TR17-TL0_S1 | 6-BK-6_TN-1_TR17-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2418 | PCU06.INV17-BK-6_TN-1_TR18-TL0_S0 | 6-BK-6_TN-1_TR18-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2419 | PCU06.INV17-BK-6_TN-1_TR18-TL0_S1 | 6-BK-6_TN-1_TR18-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2420 | PCU06.INV17-BK-6_TN-1_TR19-TL0_S0 | 6-BK-6_TN-1_TR19-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2421 | PCU06.INV17-BK-6_TN-1_TR19-TL0_S1 | 6-BK-6_TN-1_TR19-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2422 | PCU06.INV17-BK-6_TN-1_TR20-TL0_S0 | 6-BK-6_TN-1_TR20-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2423 | PCU06.INV17-BK-6_TN-1_TR20-TL0_S1 | 6-BK-6_TN-1_TR20-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2424 | PCU06.INV17-BK-6_TN-1_TR21-TL0_S0 | 6-BK-6_TN-1_TR21-TL0_S0 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2425 | PCU06.INV17-BK-6_TN-1_TR21-TL0_S1 | 6-BK-6_TN-1_TR21-TL0_S1 | INV17 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2426 | PCU06.INV18-BK-6_TN-1_TR22-TL0_S0 | 6-BK-6_TN-1_TR22-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2427 | PCU06.INV18-BK-6_TN-1_TR22-TL0_S1 | 6-BK-6_TN-1_TR22-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2428 | PCU06.INV18-BK-6_TN-1_TR23-TL0_S0 | 6-BK-6_TN-1_TR23-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2429 | PCU06.INV18-BK-6_TN-1_TR23-TL0_S1 | 6-BK-6_TN-1_TR23-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2430 | PCU06.INV18-BK-6_TN-1_TR24-TL0_S0 | 6-BK-6_TN-1_TR24-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2431 | PCU06.INV18-BK-6_TN-1_TR24-TL0_S1 | 6-BK-6_TN-1_TR24-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2432 | PCU06.INV18-BK-6_TN-1_TR25-TL0_S0 | 6-BK-6_TN-1_TR25-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2433 | PCU06.INV18-BK-6_TN-1_TR25-TL0_S1 | 6-BK-6_TN-1_TR25-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2434 | PCU06.INV18-BK-6_TN-1_TR26-TL0_S0 | 6-BK-6_TN-1_TR26-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2435 | PCU06.INV18-BK-6_TN-1_TR26-TL0_S1 | 6-BK-6_TN-1_TR26-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2436 | PCU06.INV18-BK-6_TN-1_TR27-TL0_S0 | 6-BK-6_TN-1_TR27-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2437 | PCU06.INV18-BK-6_TN-1_TR27-TL0_S1 | 6-BK-6_TN-1_TR27-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2438 | PCU06.INV18-BK-6_TN-1_TR28-TL0_S0 | 6-BK-6_TN-1_TR28-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2439 | PCU06.INV18-BK-6_TN-1_TR28-TL0_S1 | 6-BK-6_TN-1_TR28-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2440 | PCU06.INV18-BK-6_TN-1_TR29-TL0_S0 | 6-BK-6_TN-1_TR29-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2441 | PCU06.INV18-BK-6_TN-1_TR29-TL0_S1 | 6-BK-6_TN-1_TR29-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2442 | PCU06.INV18-BK-6_TN-1_TR30-TL0_S0 | 6-BK-6_TN-1_TR30-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2443 | PCU06.INV18-BK-6_TN-1_TR30-TL0_S1 | 6-BK-6_TN-1_TR30-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2444 | PCU06.INV18-BK-6_TN-1_TR31-TL0_S0 | 6-BK-6_TN-1_TR31-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2445 | PCU06.INV18-BK-6_TN-1_TR31-TL0_S1 | 6-BK-6_TN-1_TR31-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2446 | PCU06.INV18-BK-6_TN-1_TR32-TL0_S0 | 6-BK-6_TN-1_TR32-TL0_S0 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2447 | PCU06.INV18-BK-6_TN-1_TR32-TL0_S1 | 6-BK-6_TN-1_TR32-TL0_S1 | INV18 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2448 | PCU06.INV19-BK-6_TN-1_TR33-TL0_S0 | 6-BK-6_TN-1_TR33-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2449 | PCU06.INV19-BK-6_TN-1_TR33-TL0_S1 | 6-BK-6_TN-1_TR33-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2450 | PCU06.INV19-BK-6_TN-1_TR34-TL0_S0 | 6-BK-6_TN-1_TR34-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2451 | PCU06.INV19-BK-6_TN-1_TR34-TL0_S1 | 6-BK-6_TN-1_TR34-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2452 | PCU06.INV19-BK-6_TN-1_TR35-TL0_S0 | 6-BK-6_TN-1_TR35-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2453 | PCU06.INV19-BK-6_TN-1_TR35-TL0_S1 | 6-BK-6_TN-1_TR35-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2454 | PCU06.INV19-BK-6_TN-1_TR36-TL0_S0 | 6-BK-6_TN-1_TR36-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2455 | PCU06.INV19-BK-6_TN-1_TR36-TL0_S1 | 6-BK-6_TN-1_TR36-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2456 | PCU06.INV19-BK-6_TN-1_TR37-TL0_S0 | 6-BK-6_TN-1_TR37-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2457 | PCU06.INV19-BK-6_TN-1_TR37-TL0_S1 | 6-BK-6_TN-1_TR37-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2458 | PCU06.INV19-BK-6_TN-1_TR38-TL0_S0 | 6-BK-6_TN-1_TR38-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2459 | PCU06.INV19-BK-6_TN-1_TR38-TL0_S1 | 6-BK-6_TN-1_TR38-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2460 | PCU06.INV19-BK-6_TN-1_TR39-TL0_S0 | 6-BK-6_TN-1_TR39-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2461 | PCU06.INV19-BK-6_TN-1_TR39-TL0_S1 | 6-BK-6_TN-1_TR39-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2462 | PCU06.INV19-BK-6_TN-1_TR40-TL0_S0 | 6-BK-6_TN-1_TR40-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2463 | PCU06.INV19-BK-6_TN-1_TR40-TL0_S1 | 6-BK-6_TN-1_TR40-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2464 | PCU06.INV19-BK-6_TN-1_TR41-TL0_S0 | 6-BK-6_TN-1_TR41-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2465 | PCU06.INV19-BK-6_TN-1_TR41-TL0_S1 | 6-BK-6_TN-1_TR41-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2466 | PCU06.INV19-BK-6_TN-1_TR42-TL0_S0 | 6-BK-6_TN-1_TR42-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2467 | PCU06.INV19-BK-6_TN-1_TR42-TL0_S1 | 6-BK-6_TN-1_TR42-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91
2468 | PCU06.INV19-BK-6_TN-1_TR43-TL0_S0 | 6-BK-6_TN-1_TR43-TL0_S0 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 64.03 | 32.02 | 32.02 | 27.5 | 1061.2 | 17.31 | 0 | 4.79 | 4.79 | 0.45 | 82.94 | 0.45
2469 | PCU06.INV19-BK-6_TN-1_TR43-TL0_S1 | 6-BK-6_TN-1_TR43-TL0_S1 | INV19 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 138.86 | 69.43 | 69.43 | 27.5 | 1061.2 | 17.31 | 0 | 10.39 | 10.39 | 0.98 | 179.86 | 0.98
2470 | PCU06.INV20-BK-6_TN-0_TR46-TL0_S0 | 6-BK-6_TN-0_TR46-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 195.03 | 97.51 | 97.51 | 21.28 | 1061.2 | 17.31 | 0 | 14.59 | 14.59 | 1.38 | 252.6 | 1.38
2471 | PCU06.INV20-BK-6_TN-0_TR46-TL0_S1 | 6-BK-6_TN-0_TR46-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 120.2 | 60.1 | 60.1 | 21.28 | 1061.2 | 17.31 | 0 | 8.99 | 8.99 | 0.85 | 155.68 | 0.85
2472 | PCU06.INV20-BK-6_TN-0_TR47-TL0_S0 | 6-BK-6_TN-0_TR47-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 184.93 | 92.46 | 92.46 | 16.28 | 1061.2 | 17.31 | 0 | 13.84 | 13.84 | 1.3 | 239.52 | 1.31
2473 | PCU06.INV20-BK-6_TN-0_TR47-TL0_S1 | 6-BK-6_TN-0_TR47-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 110.1 | 55.05 | 55.05 | 16.28 | 1061.2 | 17.31 | 0 | 8.24 | 8.24 | 0.78 | 142.6 | 0.78
2474 | PCU06.INV20-BK-6_TN-0_TR48-TL0_S0 | 6-BK-6_TN-0_TR48-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 174.83 | 87.41 | 87.41 | 11.28 | 1061.2 | 17.31 | 0 | 13.08 | 13.08 | 1.23 | 226.44 | 1.23
2475 | PCU06.INV20-BK-6_TN-0_TR48-TL0_S1 | 6-BK-6_TN-0_TR48-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 100 | 50 | 50 | 11.28 | 1061.2 | 17.31 | 0 | 7.48 | 7.48 | 0.71 | 129.52 | 0.71
2476 | PCU06.INV20-BK-6_TN-0_TR49-TL0_S0 | 6-BK-6_TN-0_TR49-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 164.73 | 82.36 | 82.36 | 6.28 | 1061.2 | 17.31 | 0 | 12.33 | 12.33 | 1.16 | 213.35 | 1.16
2477 | PCU06.INV20-BK-6_TN-0_TR49-TL0_S1 | 6-BK-6_TN-0_TR49-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 89.9 | 44.95 | 44.95 | 6.28 | 1061.2 | 17.31 | 0 | 6.73 | 6.73 | 0.63 | 116.43 | 0.63
2478 | PCU06.INV20-BK-6_TN-0_TR50-TL0_S0 | 6-BK-6_TN-0_TR50-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 174.83 | 87.41 | 87.41 | 11.28 | 1061.2 | 17.31 | 0 | 13.08 | 13.08 | 1.23 | 226.44 | 1.23
2479 | PCU06.INV20-BK-6_TN-1_TR44-TL0_S0 | 6-BK-6_TN-1_TR44-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2480 | PCU06.INV20-BK-6_TN-1_TR44-TL0_S1 | 6-BK-6_TN-1_TR44-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2481 | PCU06.INV20-BK-6_TN-1_TR45-TL0_S0 | 6-BK-6_TN-1_TR45-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2482 | PCU06.INV20-BK-6_TN-1_TR45-TL0_S1 | 6-BK-6_TN-1_TR45-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2483 | PCU06.INV20-BK-6_TN-1_TR46-TL0_S0 | 6-BK-6_TN-1_TR46-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 13.53 | 6.77 | 6.77 | 2.5 | 1061.2 | 17.31 | 0 | 1.01 | 1.01 | 0.1 | 17.53 | 0.1
2484 | PCU06.INV20-BK-6_TN-1_TR46-TL0_S1 | 6-BK-6_TN-1_TR46-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 88.36 | 44.18 | 44.18 | 2.5 | 1061.2 | 17.31 | 0 | 6.61 | 6.61 | 0.62 | 114.45 | 0.62
2485 | PCU06.INV20-BK-6_TN-1_TR47-TL0_S0 | 6-BK-6_TN-1_TR47-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 23.63 | 11.82 | 11.82 | 7.5 | 1061.2 | 17.31 | 0 | 1.77 | 1.77 | 0.17 | 30.61 | 0.17
2486 | PCU06.INV20-BK-6_TN-1_TR47-TL0_S1 | 6-BK-6_TN-1_TR47-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 98.46 | 49.23 | 49.23 | 7.5 | 1061.2 | 17.31 | 0 | 7.37 | 7.37 | 0.69 | 127.53 | 0.7
2487 | PCU06.INV20-BK-6_TN-1_TR48-TL0_S0 | 6-BK-6_TN-1_TR48-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 33.73 | 16.87 | 16.87 | 12.5 | 1061.2 | 17.31 | 0 | 2.52 | 2.52 | 0.24 | 43.69 | 0.24
2488 | PCU06.INV20-BK-6_TN-1_TR48-TL0_S1 | 6-BK-6_TN-1_TR48-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 108.56 | 54.28 | 54.28 | 12.5 | 1061.2 | 17.31 | 0 | 8.12 | 8.12 | 0.77 | 140.61 | 0.77
2489 | PCU06.INV20-BK-6_TN-1_TR49-TL0_S0 | 6-BK-6_TN-1_TR49-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 43.83 | 21.92 | 21.92 | 17.5 | 1061.2 | 17.31 | 0 | 3.28 | 3.28 | 0.31 | 56.77 | 0.31
2490 | PCU06.INV20-BK-6_TN-1_TR49-TL0_S1 | 6-BK-6_TN-1_TR49-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 118.66 | 59.33 | 59.33 | 17.5 | 1061.2 | 17.31 | 0 | 8.88 | 8.88 | 0.84 | 153.7 | 0.84
2491 | PCU06.INV20-BK-6_TN-1_TR50-TL0_S0 | 6-BK-6_TN-1_TR50-TL0_S0 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 53.93 | 26.97 | 26.97 | 22.5 | 1061.2 | 17.31 | 0 | 4.04 | 4.04 | 0.38 | 69.86 | 0.38
2492 | PCU06.INV20-BK-6_TN-1_TR50-TL0_S1 | 6-BK-6_TN-1_TR50-TL0_S1 | INV20 | Helokabel | SOLARFLEX-X PV1-F(6mm) | 6 | 6 | 5.9 | 23.6 | 128.76 | 64.38 | 64.38 | 22.5 | 1061.2 | 17.31 | 0 | 9.63 | 9.63 | 0.91 | 166.78 | 0.91